## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5200 | 5206 | 4300 | 4290 | 900 | 916 | 17.31% | 17.6%
RTU-2 | KITCHEN | 5000 | 5130 | 4050 | 4151 | 950 | 979 | 19% | 19.08%
RTU-3OA | OA RTU | 3250 | 4062 | 1250 | 1441 | 2000 | 2621 | 61.54% | 64.52%
PRV-2 | HD1 GRIDDLE | [10 empty] | 1500 | 1507
PRV-3 | HD2 FRYERS | [10 empty] | 1500 | 1480
PRV-4 | HD3 DISH | [10 empty] | 350 | 362
EF-1 | MENS RR | [12 empty] | 220 | 201
EF-2 | MOP ROOM | [12 empty] | 50 | 53
EF-3 (3) | WOMENS/EMPL. RR | [12 empty] | 210 | 208
TOTALS |  | 13450 | 14398 | 9600 | 9882 | 3850 | 4516 |  |  | 0 | 0 | 3350 | 3349 | 480 | 462
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3850 | 4516 |  | FRONT |  | 0.0024 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3830 | 3811 |  | SIDE |  | 0.0014 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 20 | 705 |  | REAR |  | 0.0174 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0070667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
RTU3-OA NEW SHEAVE HAS BEEN ORDERED TO BRING INTO DESIGN.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0