## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 4020 | 3500 | 3520 | 500 | 500 | 12.5% | 12.44%
RTU-2 | DINING | 4400 | 4449 | 3400 | 3449 | 1000 | 1000 | 22.73% | 22.48%
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1403
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2566
EF-2 | RESTROOM | [12 empty] | 200 | 204
TOTALS |  | 8400 | 8469 | 6900 | 6969 | 1500 | 1500 |  |  | 1300 | 1403 | 2550 | 2566 | 200 | 204
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2903 |  | FRONT | [10 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2750 | 2770 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 133 |  | REAR |  | 0.0068 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0068 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Due to windy conditions, OA couldn't be read. OA was confirmed with building pressure at the side of the building where wind was lightest.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250