## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | CHECK OUT | 10500 | 10250 | 8500 | 8734 | 2000 | 1516 | 19.05% | 14.79%
RTU-2 | SALES | 5000 | 6404 | 4000 | 6404 | 1000 | 0 | 20% | 0%
RTU-3 | SALES | 5000 | 1745 | 4000 | 1745 | 1000 | 0 | 20% | 0%
RTU-4 | SALES | 5000 | 5715 | 4000 | 5715 | 1000 | 0 | 20% | 0%
RTU-5 | SALES | 5000 | 2655 | 5000 | 2324 | 0 | 331 | 0% | 12.47%
RTU-6 | SALES | 5000 | 3939 | 5000 | 3515 | 0 | 424 | 0% | 10.76%
RTU-7 | SALES | 5000 | 2321 | 4000 | 2321 | 1000 | 0 | 20% | 0%
RTU-8 | SALES | 5000 | 2188 | 4000 | 1910 | 1000 | 278 | 20% | 12.71%
RTU-9 | BOH | 2800 | 2790 | 2450 | 2790 | 350 | 0 | 12.5% | 0%
RTU-10 | OFFICES | 3200 | 2941 | 2850 | 2774 | 350 | 167 | 10.94% | 5.678%
RTU-11 | HALLWAY | 4000 | 0 | 3575 | 0 | 425 | 0 | 10.62% | #DIV/0!
RTU-12 | FOOD AREA | 5200 | 4819 | 4650 | 4111 | 550 | 708 | 10.58% | 14.69%
RTU-13 | ENTRANCE/EXIT | 4400 | 2974 | 3400 | 2423 | 1000 | 551 | 22.73% | 18.53%
RTU-14 | PHARMACY | 1600 | 751 | 1340 | 751 | 260 | 0 | 16.25% | 0%
EF-5 | KITCHEN HD | [10 empty] | 3150 | 2808
EF-1 | ELECTRICAL | [12 empty] | [1] | 0
EF-2 | RESTROOM | [12 empty] | 200 | 182
EF-3 | MEAT/SEAFOOD | [12 empty] | 1200 | 1298
EF-4 | BAKERY | [12 empty] | 900 | 1316
EF-6 | RESTROOM | [12 empty] | 600 | 246
EF-7 | RESTROOM | [12 empty] | 100 | 0
TOTALS |  | 66700 | 49492 | 56765 | 45517 | 9935 | 3975 |  |  | 0 | 0 | 3150 | 2808 | 3000 | 3042
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 9935 | 3975 |  | FRONT |  | [2] | [8 empty] | #DIV/0! | #DIV/0! | TRUE
TOTAL EXHAUST |  | 6150 | 5850 |  | SIDE |  | [2] |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 3785 | -1875 |  | REAR |  | [2] | [8 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
[1] NO DESIGN SHOWN ON DRAWINGS. NO SCHEDULE PROVIDED. [2] UNABLE TO OBTAIN BUILDING PRESSURE DUE TO STORE BEING OPEN AND NOT ABLE TO TAKE PRESSURE WITH ALL DOORS CLOSED AT THE SAME TIME.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0