## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8905 | 8450 | 7809 | 1050 | 1096 | 11.05% | 12.31%
AC-2 | SERVING | 5250 | 5040 | 3675 | 3415 | 1575 | 1625 | 30% | 32.24%
AC-3 | DINING | 6000 | 6236 | 3975 | 4149 | 2025 | 2087 | 33.75% | 33.47%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1869
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1280
EF-3 | RESTROOM | [12 empty] | 300 | 306
TOTALS |  | 20750 | 20181 | 16100 | 15373 | 4650 | 4808 |  |  | 0 | 0 | 3315 | 3149 | 300 | 306
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4808 |  | FRONT |  | 0.0123 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3455 |  | SIDE |  | 0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1035 | 1353 |  | REAR |  | 0.0087 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0083333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390