## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 786 | 350 | 320
RTU-2 | SALES | 800 | 793 | 350 | 341
RTU-3 | BOH/KITCHEN | 800 | 779 | 350 | 316
EF-1 | WOMEN'S RR |  |  |  |  | 225 | 378 | 225 | 378
EF-2 | MEN'S RR |  |  |  |  | 525 | 525 | 525 | 525
EF-3 | HOOD |  |  |  |  | 1350 | 1310 | 0 | 0
TOTALS |  | 2400 | 2358 | 1050 | 977 | 2100 | 2213 | 750 | 903
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2358 |  |  | FRONT |  | 0.0221 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 2213 |  |  | SIDE |  | 0.0023
NET AIRFLOW |  | 300 | 145 |  |  | REAR |  | 0.0107 |  | TRUE
[6 empty] | AVERAGE |  | 0.0117
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 977 |  |  | FRONT |  | 0.0034
TOTAL EXHAUST |  | 750 | 903 |  |  | SIDE |  | 0.0014
NET AIRFLOW |  | 300 | 74 |  |  | REAR |  | 0.0083
[6 empty] | AVERAGE |  | 0.0043667
NOTES: