## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 5089 | 4200 | 4214 | 800 | 875 | 16% | 17.19%
RTU-2 | KITCHEN | 3800 | 3731 | 3380 | 3282 | 420 | 449 | 11.05% | 12.03%
MUA-1 | COOKLINE | [8 empty] | 1976 | 2056
EF-1 | HOOD 1 | [10 empty] | 2381 | 2402
EF-2 | RESTROOMS | [12 empty] | 500 | 648
TOTALS |  | 8800 | 8820 | 7580 | 7496 | 1220 | 1324 |  |  | 1976 | 2056 | 2381 | 2402 | 500 | 648
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3196 | 3380 |  | FRONT |  | -0.22 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2881 | 3050 |  | SIDE |  | -0.2 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 315 | 330 |  | REAR |  | -0.19 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.20333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
Base line building pressure with no fans running is -0.18". Tech is unable to overcome baseline building negative pressure.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0