## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3500 | 3825 | 2620 | 2900 | 880 | 925 | 25.14% | 24.18%
RTU-2 | KITCHEN | 2400 | 2491 | 1680 | 1780 | 720 | 711 | 30% | 28.54%
MUA-1 | COOKLINE | [8 empty] | 2821 | 2878
KEF-1 | FRYER HD | [10 empty] | 1852 | 1891
KEF-2 | GRILL HD | [10 empty] | 1662 | 1691
CEF-1 | RESTROOMS | [12 empty] | 800 | 841
TOTALS |  | 5900 | 6316 | 4300 | 4680 | 1600 | 1636 |  |  | 2821 | 2878 | 3514 | 3582 | 800 | 841
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4421 | 4514 |  | FRONT |  | -0.0127 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 4314 | 4423 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 107 | 91 |  | REAR |  | -0.005 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.00885 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0