## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
OAHU-R-1 | WSHP&HOODS | 7500 | 7813 | 0 | 0 | 7500 | 7813 | 100% | 100%
PCU-1 | KH 1-3 | [10 empty] | 6383 | 6028
EF-1 | RESTROOMS | [12 empty] | 750 | 768
EF-2 | DISH HD | [10 empty] | 1050 | 952
TOTALS |  | 7500 | 7813 | 0 | 0 | 7500 | 7813 |  |  | 0 | 0 | 7433 | 6980 | 750 | 768
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 7500 | 7813 |  | FRONT |  | 0.0024 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 8183 | 7748 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -683 | 65 |  | REAR |  | -0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0007 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0