## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3394 | 3422 | 3044 | 3062 | 350 | 360 | 10.31% | 10.52%
RTU-2 | DINING | 4000 | 4250 | 3350 | 3572 | 650 | 678 | 16.25% | 15.95%
MUA-1 | KITCHEN HOOD | [8 empty] | 1965 | 2046
EF-1 | KITCHEN HOOD | [10 empty] | 2381 | 2413
EF-2 | RESTROOM | [12 empty] | 250 | 489
TOTALS |  | 7394 | 7672 | 6394 | 6634 | 1000 | 1038 |  |  | 1965 | 2046 | 2381 | 2413 | 250 | 489
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2965 | 3084 |  | FRONT |  | 0.0023 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2631 | 2902 |  | SIDE |  | -0.002 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 334 | 182 |  | REAR |  | 0.0003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0002 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250