## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | PRIVATE DINING | 1200 | 1594 | 900 | 1292 | 300 | 302 | 25% | 18.95%
RTU-2 |  | 3060 | 3062 | 2160 | 2467 | 900 | 595 | 29.41% | 19.43%
RTU-3 |  | 4200 | 4181 | 2950 | 3110 | 1250 | 1071 | 29.76% | 25.62%
RTU-4 |  | 5000 | 5553 | 3500 | 4126 | 1500 | 1427 | 30% | 25.7%
RTU-5 |  | 2175 | 2352 | 1695 | 1851 | 480 | 501 | 22.07% | 21.3%
RTU-6 |  | 4100 | 4703 | 2600 | 3403 | 1500 | 1300 | 36.59% | 27.64%
MUA-1 |  | n | [7 empty] | 2400 | 1849
MUA-2 | [9 empty] | 2730 | 2710
MUA-3 | HOOD 5 | [8 empty] | 1774 | 1894
MUA-4 | HOOD 6 & 7 | [8 empty] | 5175 | 3304
MUA-5 | HOOD 8 & 9 | [8 empty] | 1230 | 1113
KEF-1 | [11 empty] | 1500 | 1672
KEF-2 | [11 empty] | 1500 | 1622
KEF-3 | [11 empty] | 1500 | 1614
KEF-4 | [11 empty] | 1912 | 1488
KEF-5 | [11 empty] | 2383 | 2229
KEF-6 | [11 empty] | 3150 | 1903
KEF-7 | [11 empty] | 2938 | 2752
KEF-8 | [11 empty] | 788 | 724
KEF-9 | [11 empty] | 700 | 632
KEF-10 | [11 empty] | 1325 | 1197
F-7 | [13 empty] | 600 | 0
TOTALS |  | 19735 | 21445 | 13805 | 16249 | 5930 | 5196 |  |  | 13309 | 10870 | 17696 | 15833 | 600 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 19239 | 16066 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 18296 | 15833 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 943 | 233 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0