## Survey
TAB Partner - |  |  |  |  | National TAB |  |  |  | Tech- |  |  |  | IAN FULLER | [10 empty] | CONDITION SURVEY | [16 empty] | Survey Due Date - | [10 empty] | 2023-12-21
UNIT # |  |  |  | UNIT NAME | [5 empty] | STREET ADDRESS | [10 empty] | CITY | [9 empty] | ST |  | OPERATOR | [7 empty] | PHONE # | [8 empty] | EMAIL
2537 |  |  |  | Bradfordville FSU | [5 empty] | 3455 Bannerman Rd | [10 empty] | Tallahassee | [9 empty] | FL |  | Steve Elyea | [7 empty] | 8506680138 | [8 empty] | 02537@chick-fil-a.com
CONSTRUCTION MGR (CM) | [5 empty] | SR PROGRAM MGR (SRP) | [5 empty] | SR PROGRAM LEAD (SRPL) | [6 empty] | FEQ FIELD CONSULTANT | [8 empty] | PROTO-TYPE |  |  |  |  | OPEN DATE |  |  |  | UNIT AGE |  |  | CONSTR START | [6 empty] | SCOPE OF WORK | [5 empty] | ARCHITECT
Mark Farol | [5 empty] | Allison Doherty | [5 empty] | Jacob Smith | [6 empty] | Chip Phillips | [8 empty] | S08N SM |  |  |  |  | 2010-11-11 |  |  |  | 13.1918 |  |  | 2024-08-17 | [6 empty] | 3.0/BI | [5 empty] | Interplan
SYNEXIS - ACTIVE/INACTIVE/NOT INSTALLED | [25 empty] | NOT INSTALLED
AC# |  |  | SERIAL # |  |  |  | MODEL # | [6 empty] | TON |  |  | MFG. |  |  | AGE |  |  | HVAC UNIT TYPE/HUMIDITROL | [8 empty] | AREA SERVED |  |  |  |  | HEAT EXCH. |  |  | COND.DAM. |  |  |  | HAIL GARD |  |  |  |  | EVAP COIL |  | POW EXH |  | TOTAL | Marie Lisco
AC1 |  |  | 5610H10476 |  |  |  | LCH180H4BKY | [6 empty] | 15 |  |  | Lennox |  |  | 13.4712 |  |  | ENERGENCE | [8 empty] | KITCHEN |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 |  | 0
AC2 |  |  | 5610H10980 |  |  |  | LCH060H4EG1Y | [6 empty] | 5 |  |  | Lennox |  |  | 13.4712 |  |  | ENERGENCE | [8 empty] | MECH/RR/DIN A/ENT A |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 |  | 0
AC3 |  |  | 5610H10654 |  |  |  | LCH150S4BK1Y | [6 empty] | 12.5 |  |  | Lennox |  |  | 13.4712 |  |  | ENERGENCE | [8 empty] | DINB/SERV/DT |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 537 |  | 537
AC4 |  |  | 5617C06360 |  |  |  | LCH060H4EN3Y | [6 empty] | 5 |  |  | Lennox |  |  | 6.8849 |  |  | ENERGENCE | [8 empty] | PLAYLAND |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 |  | 0
AC5 |  |  | 0 |  |  |  | 0 | [9 empty] | Carrier |  |  | 0 |  |  | L SERIES | [13 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 |  | 0
AC6 |  |  | 0 |  |  |  | 0 | [9 empty] | Carrier |  |  | 0 |  |  | L SERIES | [13 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 |  | 0
AC7 |  |  | 0 |  |  |  | 0 | [9 empty] | Carrier |  |  | 0 |  |  | L SERIES | [13 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 |  | 0
AC8 | [31 empty] | TOTAL |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 537 |  | 537
CRITICAL - Unable to Perform T & B Scope until Corrected by Responsible Party.
REVIEW & RECTIFY - If no action is taken T&B can be performed, but system performance will suffer.
NON-CRITICAL - Noted for consideration by project team, but not critical to system performance or fnctionality.
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states.
|  | NON-CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A | AC3 |  |  | 12.5 |  | AC4 |  |  | N/A |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | 5 |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
7. Is unit a humiditrol type unit?
|  | NON CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  | 0 |  | AC6 |  | NO |  | AC7 | [5 empty] | AC8 |  |  | N/A
8. Is the humidity sensor wired? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  |  | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in.
|  | CRITICAL | [6 empty] | B1 |  |  | 0 |  |  | B2 |  |  | 0 | B3 |  |  | 0 |  | B4 |  |  | 0 |  |  | B5 |  |  | 0 |  | B6 |  | 0 |  | B7 | [5 empty] | B8
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in.
|  | CRITICAL | [6 empty] | D1 |  |  | 0 |  |  | D2 |  |  | 0 | D3 |  |  | 0 |  | D4 |  |  | 0 |  |  | D5 |  |  | 0 |  | D6 |  | 0 |  | D7 |  |  | 0 |  |  | D8
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
|  | CRITICAL | [6 empty] | AC1 |  |  | 0 |  |  | AC2 |  |  | 0 | AC3 |  |  |  |  | AC4 |  |  | 0 |  |  | AC5 |  |  | 0 |  | AC6 |  |  |  | AC7 | [5 empty] | AC8
12. Is a smoke detector present in unit? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A | AC3 |  |  | N/A |  | AC4 |  |  | N/A |  |  | AC5 |  |  | #VALUE! |  | AC6 |  | #VALUE! |  | AC7 |  |  | #VALUE! |  |  | AC8 |  |  | N/A
17. Is belt tensioner installed? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A | AC3 |  |  | N/A |  | AC4 |  |  | N/A |  |  | AC5 |  |  | #VALUE! |  | AC6 |  | #VALUE! |  | AC7 |  |  | #VALUE! |  |  | AC8 |  |  | N/A
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | N/A |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
19. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A | AC3 |  |  | C |  | AC4 |  |  | N/A |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
20. Record belt size.
|  | N/A | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A | AC3 |  |  | BX66 |  | AC4 |  |  | N/A |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
21. Identify any damage to the blower. If DAMAGE found, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
22. Quantify cleanliness of blower. If dirty, enter unit tonnage.
|  | NON CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | 5 | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
23. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
24. Is blank plate secured on B-cabinets? If NO, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A | AC3 |  |  | C |  | AC4 |  |  | N/A |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
25. Is ductwork lined? If YES, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
26. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
27. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
28. Is duct work seated and aligned? If NO, enter unit tonnage.
|  | N/A | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 | [5 empty] | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
29. Is canvas connector present? If NO, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
30. Quantify cleanliness of duct. If dirty, enter unit tonnage.
|  | NON CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
31. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A | AC3 |  |  | N/A |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
32. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit).
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  | #VALUE! |  | AC6 |  | #VALUE! |  | AC7 |  |  | #VALUE! |  |  | AC8 |  |  | N/A
33. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | R | AC3 |  |  | R |  | AC4 |  |  | N |  |  | AC5 |  |  | #VALUE! |  | AC6 |  | #VALUE! |  | AC7 |  |  | #VALUE! |  |  | AC8 |  |  | N/A
34. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
35. Are actuator gears worn? If yes, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  | N/A |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
36. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
37. Is there any play in the actuator gear box? If yes, enter unit tonnage
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
38. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  |  |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
39. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage.
|  | NON CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
40. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | 1 |  |  | AC2 |  |  | 1 | AC3 |  |  | 1 |  | AC4 |  |  | 1 |  |  | AC5 |  |  | 0 |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
41. Do condensation traps meet provided detail. If NO, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | NO |  |  | AC2 |  |  | 5 | AC3 |  |  | 12.5 |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
42. Do pre-filters need to be cleaned? If YES, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | 15 |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
43. Do pre-filters need to be replaced? If YES, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C | AC3 |  |  | C |  | AC4 |  |  | C |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
44. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below.
|  | CRITICAL | [6 empty] | AC1 |  |  | 15 |  |  | AC2 |  |  | 5 | AC3 |  |  | 12.5 |  | AC4 |  |  | 5 |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8 |  |  | N/A
45. Is bathroom exhaust fan running? Enter YES or NO. | [22 empty] | NO
46. Is bathroom exhaust fan making excessive noise? Enter Yes or NO. | [28 empty] | N/A
47. Is bathroom exhaust fan vibrating excessively? Enter YES or NO. | [27 empty] | N/A
48. Does bathroom exhaust fan have a back draft damper? Enter YES or NO. | [31 empty] | YES
49. Does bathroom exhaust fan duct have a liner? Enter YES OR NO. | [26 empty] | YES
50. Visually inspect ductwork at bathroom exhaust fan, and rate cleanliness. Enter CLEAN OR DIRTY. | [40 empty] | DIRTY
51. Record model number of Suncoast Panel. | [18 empty] | Model # | [6 empty] | CHICK-FIL-A CONTROL PANEL
52. Record serial number of Suncoast Panel. | [18 empty] | Serial # | [6 empty] | 10-CFA-052
53. Is there a HES control panel visible? Enter YES or NO. | [25 empty] | YES
54. Are thermostats Robert Shaw (Gray Display) or Network (Blue Display) ? Enter "RS", "NW" for Robert Shaw and Network respectively. If thermostat not Robert Shaw or Network, enter NO. | [24 empty] | AC1 |  |  | RS |  |  | AC2 |  |  | RS |  | AC3 |  | RS |  | AC4 |  |  | RS |  |  | AC5 |  |  | 0
[25 empty] | AC6 |  |  | 0 |  |  | AC7 |  |  | 0 |  | AC8 |  | 0
MISCELLANEOUS NOTES
RTU 1 |  |  | OUTSIDE AIR ECONOMIZER BLADE DAMPERS ARE NOT ATTACHED TO GEAR BOX
MISSING RETURN AIR BLADE DAMPERS
0
RTU 2 |  |  | 0
0
0
RTU 3 |  |  | 0
0
0
RTU 4 |  |  | 0
0
0
RTU 5 |  |  | 0
0
0
RTU 6 |  |  | 0
MISC NOTES |  |  | 0
DEVELOPED LENGTH ______ ' - 2018 INTERNATIONAL FUEL GAS CODE - BRANCH LENGTH METHOD - TOTAL BTU'S _________
|  | BRANCH PIPING (B#) | [18 empty] | DROP PIPING (D#)
|  | DESCRIPTION |  |  |  | BRANCH LENGTH/SIZE | [14 empty] | DESCRIPTION | [12 empty] | DROP LENGTH/SIZE | [16 empty] | PIPE SIZE |  | *OUTSIDE DIAMETER
|  | GAS LINE |  |  |  | LENGTH |  | AS-BUILT |  |  | DESIGN |  |  |  |  | CALC |  |  |  |  | DROP |  |  | GAS LINE |  |  |  |  | DEVICE |  |  |  |  | LENGTH |  |  | AS-BUILT |  |  |  |  | DESIGN |  |  |  |  | CALC
[6 empty] | (ft) |  | (in) |  |  | (in) |  |  |  |  | (in) | [17 empty] | (ft) |  |  | (in) |  |  |  |  | (in) |  |  |  |  | (in) |  |  |  | 1/2" |  | 7/8"
|  | Meter to B1 | [18 empty] | D1 |  |  | B1 to |  |  |  |  | WH | [21 empty] | 3/4" |  | 1"
|  | B1 to B2 | [18 empty] | D2 |  |  | B2 to |  |  |  |  | RTU 1 | [21 empty] | 1" |  | 1-5/16"
|  | B2 to B3 | [18 empty] | D3 |  |  | B3 to |  |  |  |  | RTU 2 | [21 empty] | 1-1/4" |  | 1-5/8"
|  | B3 to B4 | [18 empty] | D4 |  |  | B4 to |  |  |  |  | RTU 4 | [21 empty] | 1-1/2" |  | 1-7/8"
|  | B4 to B5 | [18 empty] | D5 |  |  | B5 to |  |  |  |  | RTU 3 | [21 empty] | 2" |  | 2-3/8"
|  | D6 | [18 empty] | D6 |  |  | B6 to |  |  |  |  | RTU 5 | [21 empty] | 2-1/2" |  | 2-7/8"
[51 empty] | 3' |  | 3-1/2"
[51 empty] | 3-1/2" |  | 4"
[51 empty] | 4" |  | 4-1/2"
*Approximate
NO GAS LINES INSTALLED ON UNITS. ELECTRICAL UNITS.
ROOFTOP VIEW #1 | [22 empty] | ROOFTOP VIEW #2
BROKEN ECONOMIZER AC#1 | [22 empty] | AC#4 CURB ADAPTOR
AC#2 DIRTY BLOWER WHEEL | [22 empty] | MISSING POWER EXHAUST AC#3
SUNCOAST PANEL DOES NOT HAVE SINGLE TWISTED PAIR WITH DRAIN WIRE | [22 empty] | INSERT 8
INSERT 9 | [22 empty] | INSERT 10
INSERT 11 | [22 empty] | INSERT 12
Formulas:
UNIT AGE = (TODAY()-[OPERATOR])/365

## RTU1
RTU UNIT MANUFACTURER |  | Lennox
RTU TYPE |  | ENERGENCE
MODEL NUMBER |  | LCH180H4BKY
SERIAL NUMBER |  | 5610H10476
| RTU AGE |  | 13.4712 | RTU TONNAGE | 15
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out. |  |  |  |  | C | 0
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage. |  |  |  |  | N/A
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states. |  |  |  |  | N/A
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage |  |  |  |  | N/A
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage. |  |  |  |  | N/A
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage. |  |  |  |  | N/A
7. Is unit a humiditrol type unit? |  |  |  |  | C
8. Is the humidity sensor wired? If NO, enter unit tonnage. |  |  |  |  | C
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in. |  |  |  |  | 0
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in. |  |  |  |  | 0
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
12. Is a smoke detector present in unit? If NO, enter unit tonnage. |  |  |  |  | C
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage. |  |  |  |  | C
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage. |  |  |  |  | C
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage. |  |  |  |  | C
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage. |  |  |  |  | N/A
17. Is belt tensioner installed? If NO, enter unit tonnage. |  |  |  |  | N/A
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage. |  |  |  |  | N/A
19. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes. |  |  |  |  | N/A
20. Record belt size. |  |  |  |  | N/A
21. Identify any damage to the blower. If DAMAGE found, enter unit tonnage. |  |  |  |  | N/A
22. Quantify cleanliness of blower. If dirty, enter unit tonnage. |  |  |  |  | N/A
23. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage. |  |  |  |  | N/A
24. Is blank plate secured on B-cabinets? If NO, enter unit tonnage. |  |  |  |  | N/A
25. Is ductwork lined? If YES, enter unit tonnage. |  |  |  |  | N/A
26. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage. |  |  |  |  | N/A
27. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage. |  |  |  |  | N/A
28. Is duct work seated and aligned? If NO, enter unit tonnage. |  |  |  |  | N/A
29. Is canvas connector present? If NO, enter unit tonnage. |  |  |  |  | N/A
30. Quantify cleanliness of duct. If dirty, enter unit tonnage. |  |  |  |  | N/A
31. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage. |  |  |  |  | N/A
32. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit). |  |  |  |  | N/A
33. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R. |  |  |  |  | N/A
34. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage. |  |  |  |  | N/A
35. Are actuator gears worn? If yes, enter unit tonnage. |  |  |  |  | N/A
36. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage. |  |  |  |  | N/A
37. Is there any play in the actuator gear box? If yes, enter unit tonnage |  |  |  |  | N/A
38. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent. |  |  |  |  | C
39. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage. |  |  |  |  | C
40. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE. |  |  |  |  | 1
41. Do condensation traps meet provided detail. If NO, enter unit tonnage. |  |  |  |  | NO
42. Do pre-filters need to be cleaned? If YES, enter unit tonnage. |  |  |  |  | 15
43. Do pre-filters need to be replaced? If YES, enter unit tonnage. |  |  |  |  | C
44. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below. |  |  |  |  | 15
MISCELLENOUS NOTES
OUTSIDE AIR ECONOMIZER BLADE DAMPERS ARE NOT ATTACHED TO GEAR BOX
MISSING RETURN AIR BLADE DAMPERS

## RTU2
RTU UNIT MANUFACTURER |  | Lennox
RTU TYPE |  | ENERGENCE
MODEL NUMBER |  | LCH060H4EG1Y
SERIAL NUMBER |  | 5610H10980
| RTU AGE |  | 13.4712 | RTU TONNAGE | 5
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out. |  |  |  |  | C | 0
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage. |  |  |  |  | C
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states. |  |  |  |  | C
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage |  |  |  |  | C
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage. |  |  |  |  | N/A
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage. |  |  |  |  | C
7. Is unit a humiditrol type unit? |  |  |  |  | C
8. Is the humidity sensor wired? If NO, enter unit tonnage. |  |  |  |  | C
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in. |  |  |  |  | 0
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in. |  |  |  |  | 0
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
12. Is a smoke detector present in unit? If NO, enter unit tonnage. |  |  |  |  | C
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage. |  |  |  |  | C
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage. |  |  |  |  | C
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage. |  |  |  |  | C
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage. |  |  |  |  | N/A
17. Is belt tensioner installed? If NO, enter unit tonnage. |  |  |  |  | N/A
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage. |  |  |  |  | C
19. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes. |  |  |  |  | N/A
20. Record belt size. |  |  |  |  | N/A
21. Identify any damage to the blower. If DAMAGE found, enter unit tonnage. |  |  |  |  | C
22. Quantify cleanliness of blower. If dirty, enter unit tonnage. |  |  |  |  | 5
23. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage. |  |  |  |  | C
24. Is blank plate secured on B-cabinets? If NO, enter unit tonnage. |  |  |  |  | N/A
25. Is ductwork lined? If YES, enter unit tonnage. |  |  |  |  | C
26. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage. |  |  |  |  | C
27. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage. |  |  |  |  | C
28. Is duct work seated and aligned? If NO, enter unit tonnage. |  |  |  |  | C
29. Is canvas connector present? If NO, enter unit tonnage. |  |  |  |  | C
30. Quantify cleanliness of duct. If dirty, enter unit tonnage. |  |  |  |  | C
31. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage. |  |  |  |  | N/A
32. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit). |  |  |  |  | C
33. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R. |  |  |  |  | R
34. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage. |  |  |  |  | C
35. Are actuator gears worn? If yes, enter unit tonnage. |  |  |  |  | C
36. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage. |  |  |  |  | C
37. Is there any play in the actuator gear box? If yes, enter unit tonnage |  |  |  |  | C
38. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent. |  |  |  |  | C
39. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage. |  |  |  |  | C
40. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE. |  |  |  |  | 1
41. Do condensation traps meet provided detail. If NO, enter unit tonnage. |  |  |  |  | 5
42. Do pre-filters need to be cleaned? If YES, enter unit tonnage. |  |  |  |  | C
43. Do pre-filters need to be replaced? If YES, enter unit tonnage. |  |  |  |  | C
44. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below. |  |  |  |  | 5
MISCELLENOUS NOTES

## RTU3
RTU UNIT MANUFACTURER |  | Lennox
RTU TYPE |  | ENERGENCE
MODEL NUMBER |  | LCH150S4BK1Y
SERIAL NUMBER |  | 5610H10654
| RTU AGE |  | 13.4712 | RTU TONNAGE | 12.5
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out. |  |  |  |  | C | 0
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage. |  |  |  |  | C
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states. |  |  |  |  | C
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage |  |  |  |  | C
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage. |  |  |  |  | 12.5
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage. |  |  |  |  | C
7. Is unit a humiditrol type unit? |  |  |  |  | C
8. Is the humidity sensor wired? If NO, enter unit tonnage. |  |  |  |  | C
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in. |  |  |  |  | 0
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in. |  |  |  |  | 0
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
12. Is a smoke detector present in unit? If NO, enter unit tonnage. |  |  |  |  | C
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage. |  |  |  |  | C
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage. |  |  |  |  | C
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage. |  |  |  |  | C
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage. |  |  |  |  | N/A
17. Is belt tensioner installed? If NO, enter unit tonnage. |  |  |  |  | N/A
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage. |  |  |  |  | C
19. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes. |  |  |  |  | C
20. Record belt size. |  |  |  |  | BX66
21. Identify any damage to the blower. If DAMAGE found, enter unit tonnage. |  |  |  |  | C
22. Quantify cleanliness of blower. If dirty, enter unit tonnage. |  |  |  |  | C
23. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage. |  |  |  |  | C
24. Is blank plate secured on B-cabinets? If NO, enter unit tonnage. |  |  |  |  | C
25. Is ductwork lined? If YES, enter unit tonnage. |  |  |  |  | C
26. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage. |  |  |  |  | C
27. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage. |  |  |  |  | C
28. Is duct work seated and aligned? If NO, enter unit tonnage. |  |  |  |  | C
29. Is canvas connector present? If NO, enter unit tonnage. |  |  |  |  | C
30. Quantify cleanliness of duct. If dirty, enter unit tonnage. |  |  |  |  | C
31. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage. |  |  |  |  | N/A
32. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit). |  |  |  |  | C
33. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R. |  |  |  |  | R
34. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage. |  |  |  |  | C
35. Are actuator gears worn? If yes, enter unit tonnage. |  |  |  |  | C
36. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage. |  |  |  |  | C
37. Is there any play in the actuator gear box? If yes, enter unit tonnage |  |  |  |  | C
38. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent. |  |  |  |  | C
39. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage. |  |  |  |  | C
40. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE. |  |  |  |  | 1
41. Do condensation traps meet provided detail. If NO, enter unit tonnage. |  |  |  |  | 12.5
42. Do pre-filters need to be cleaned? If YES, enter unit tonnage. |  |  |  |  | C
43. Do pre-filters need to be replaced? If YES, enter unit tonnage. |  |  |  |  | C
44. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below. |  |  |  |  | 12.5
MISCELLENOUS NOTES

## RTU4
RTU UNIT MANUFACTURER |  | Lennox
RTU TYPE |  | ENERGENCE
MODEL NUMBER |  | LCH060H4EN3Y
SERIAL NUMBER |  | 5617C06360
| RTU AGE |  | 6.8849 | RTU TONNAGE | 5
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out. |  |  |  |  | C | 0
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage. |  |  |  |  | C
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states. |  |  |  |  | C
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage |  |  |  |  | C
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage. |  |  |  |  | N/A
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage. |  |  |  |  | 5
7. Is unit a humiditrol type unit? |  |  |  |  | C
8. Is the humidity sensor wired? If NO, enter unit tonnage. |  |  |  |  | C
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in. |  |  |  |  | 0
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in. |  |  |  |  | 0
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
12. Is a smoke detector present in unit? If NO, enter unit tonnage. |  |  |  |  | C
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage. |  |  |  |  | C
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage. |  |  |  |  | C
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage. |  |  |  |  | C
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage. |  |  |  |  | N/A
17. Is belt tensioner installed? If NO, enter unit tonnage. |  |  |  |  | N/A
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage. |  |  |  |  | N/A
19. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes. |  |  |  |  | N/A
20. Record belt size. |  |  |  |  | N/A
21. Identify any damage to the blower. If DAMAGE found, enter unit tonnage. |  |  |  |  | C
22. Quantify cleanliness of blower. If dirty, enter unit tonnage. |  |  |  |  | C
23. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage. |  |  |  |  | C
24. Is blank plate secured on B-cabinets? If NO, enter unit tonnage. |  |  |  |  | N/A
25. Is ductwork lined? If YES, enter unit tonnage. |  |  |  |  | C
26. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage. |  |  |  |  | C
27. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage. |  |  |  |  | C
28. Is duct work seated and aligned? If NO, enter unit tonnage. |  |  |  |  | C
29. Is canvas connector present? If NO, enter unit tonnage. |  |  |  |  | C
30. Quantify cleanliness of duct. If dirty, enter unit tonnage. |  |  |  |  | C
31. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage. |  |  |  |  | C
32. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit). |  |  |  |  | C
33. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R. |  |  |  |  | N
34. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage. |  |  |  |  | C
35. Are actuator gears worn? If yes, enter unit tonnage. |  |  |  |  | C
36. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage. |  |  |  |  | C
37. Is there any play in the actuator gear box? If yes, enter unit tonnage |  |  |  |  | C
38. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent. |  |  |  |  | C
39. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage. |  |  |  |  | C
40. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE. |  |  |  |  | 1
41. Do condensation traps meet provided detail. If NO, enter unit tonnage. |  |  |  |  | C
42. Do pre-filters need to be cleaned? If YES, enter unit tonnage. |  |  |  |  | C
43. Do pre-filters need to be replaced? If YES, enter unit tonnage. |  |  |  |  | C
44. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below. |  |  |  |  | 5
MISCELLENOUS NOTES

## RTU5
RTU UNIT MANUFACTURER |  | Carrier
RTU TYPE |  | L SERIES
MODEL NUMBER |  | 0
SERIAL NUMBER |  | 0
| RTU AGE |  | 0 | RTU TONNAGE
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out. | [5 empty] | 0
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage.
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states.
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage. |  |  |  |  | N/A
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage.
7. Is unit a humiditrol type unit?
8. Is the humidity sensor wired? If NO, enter unit tonnage.
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in. |  |  |  |  | 0
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in. |  |  |  |  | 0
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
12. Is a smoke detector present in unit? If NO, enter unit tonnage.
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage.
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage.
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage.
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage. |  |  |  |  | #VALUE!
17. Is belt tensioner installed? If NO, enter unit tonnage. |  |  |  |  | #VALUE!
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage.
19. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes.
20. Record belt size.
21. Identify any damage to the blower. If DAMAGE found, enter unit tonnage.
22. Quantify cleanliness of blower. If dirty, enter unit tonnage.
23. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage.
24. Is blank plate secured on B-cabinets? If NO, enter unit tonnage. |  |  |  |  | N/A
25. Is ductwork lined? If YES, enter unit tonnage.
26. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage.
27. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage.
28. Is duct work seated and aligned? If NO, enter unit tonnage.
29. Is canvas connector present? If NO, enter unit tonnage.
30. Quantify cleanliness of duct. If dirty, enter unit tonnage.
31. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage.
32. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit). |  |  |  |  | #VALUE!
33. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R. |  |  |  |  | #VALUE!
34. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage.
35. Are actuator gears worn? If yes, enter unit tonnage. |  |  |  |  | N/A
36. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage.
37. Is there any play in the actuator gear box? If yes, enter unit tonnage
38. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent.
39. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage.
40. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE.
41. Do condensation traps meet provided detail. If NO, enter unit tonnage.
42. Do pre-filters need to be cleaned? If YES, enter unit tonnage.
43. Do pre-filters need to be replaced? If YES, enter unit tonnage.
44. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below.
MISCELLENOUS NOTES

## RTU6
RTU UNIT MANUFACTURER | Carrier
RTU TYPE | L SERIES
MODEL NUMBER | 0
SERIAL NUMBER | 0
RTU TONNAGE
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out. |  |  | 0
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage.
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states.
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage. |  | N/A
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage.
7. Is unit a humiditrol type unit? |  | NO
8. Is the humidity sensor wired? If NO, enter unit tonnage.
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in. |  | 0
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in. |  | 0
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
12. Is a smoke detector present in unit? If NO, enter unit tonnage.
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage.
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage.
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage.
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage. |  | #VALUE!
17. Is belt tensioner installed? If NO, enter unit tonnage. |  | #VALUE!
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage. |  | N/A
19. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes. |  | N/A
20. Record belt size.
21. Identify any damage to the blower. If DAMAGE found, enter unit tonnage.
22. Quantify cleanliness of blower. If dirty, enter unit tonnage.
23. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage.
24. Is blank plate secured on B-cabinets? If NO, enter unit tonnage. |  | N/A
25. Is ductwork lined? If YES, enter unit tonnage.
26. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage.
27. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage.
28. Is duct work seated and aligned? If NO, enter unit tonnage.
29. Is canvas connector present? If NO, enter unit tonnage.
30. Quantify cleanliness of duct. If dirty, enter unit tonnage.
31. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage.
32. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit). |  | #VALUE!
33. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R. |  | #VALUE!
34. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage.
35. Are actuator gears worn? If yes, enter unit tonnage. |  | N/A
36. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage.
37. Is there any play in the actuator gear box? If yes, enter unit tonnage
38. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent.
39. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage.
40. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE.
41. Do condensation traps meet provided detail. If NO, enter unit tonnage.
42. Do pre-filters need to be cleaned? If YES, enter unit tonnage.
43. Do pre-filters need to be replaced? If YES, enter unit tonnage.
44. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below.
MISCELLENOUS NOTES

## BR EF
BATHROOM EF/SUNCOAST PANEL/ THERMOSTATS
45. Is bathroom exhaust fan running? Enter YES or NO. | [7 empty] | NO
46. Is bathroom exhaust fan making excessive noise? Enter Yes or NO. | [7 empty] | N/A
47. Is bathroom exhaust fan vibrating excessively? Enter YES or NO. | [7 empty] | N/A
48. Does bathroom exhaust fan have a back draft damper? Enter YES or NO. | [7 empty] | YES
49. Does bathroom exhaust fan duct have a liner? Enter YES OR NO. | [7 empty] | YES
50. Visually inspect ductwork at bathroom exhaust fan, and rate cleanliness. Enter CLEAN OR DIRTY. | [7 empty] | DIRTY
51. Record model number of Suncoast Panel. | [7 empty] | CHICK-FIL-A CONTROL PANEL
52. Record serial number of Suncoast Panel. | [7 empty] | 10-CFA-052
53. Is there a HES control panel visible? | [7 empty] | YES
54. Are thermostats Robert Shaw (Gray Display) or Network (Blue Display) ? Enter "RS", "NW" for Robert Shaw and Network respectively. If thermostat not Robert Shaw or Network, enter NO.
AC1 | RS | AC2 | RS | AC3 | RS | AC4 | RS | AC5
AC6 |  | AC7 |  | AC8
MISCELLENOUS NOTES

## Store Data
(2) Store No. | Survey Due Date | (8) Construction Start Date (CSD) | (3) Location Name | (4) SOW | (14) Prototype | (23) Region | TAB Partner | Street Address | City | State | (27) Operator | SR Program Lead (SRPL) | SR Development Manager (DM) | SR Construction Manager (CM) | SR Program Manager (SRP) | FEQ Field Consultant | (37) Architect | Open Date | Location Phone | Location E-mail | AC1 |  |  |  |  | AC2 |  |  |  |  | AC3 |  |  |  |  | AC4 |  |  |  |  | AC5 |  |  |  |  | AC6 |  |  |  |  | AC7 |  |  |  |  | AC8
1 |  |  | Northeast | [17 empty] | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type
2537 | 2023-12-21 | 2024-08-17 | Bradfordville FSU | 3.0/BI | S08N SM | Southeast | National TAB | 3455 Bannerman Rd | Tallahassee | FL | Steve Elyea | Jacob Smith | Marie Lisco | Mark Farol | Allison Doherty | Chip Phillips | Interplan | 2010-11-11 | 8506680138 | 02537@chick-fil-a.com | 5610H10476 | LCH180H4BKY | 2010-08-01 | 13.4712 | ENER | 5610H10980 | LCH060H4EG1Y | 2010-08-01 | 13.4712 | ENER | 5610H10654 | LCH150S4BK1Y | 2010-08-01 | 13.4712 | ENER | 5617C06360 | LCH060H4EN3Y | 2017-03-01 | 6.8849 | ENER
[46 empty] | 5614G02828 | LCH120H4BN3Y | 2014-07-01
Formulas:
Age = (TODAY()-[Mfg Date])/365
Note on C10: 10/26/22 CSD ENTERED -Mark

## Drop Menus
DEVICE | GAS PIPE SIZE | CONDENSATION | DROP
PIPE SIZE
WH | 1/2" | 0.75 | D1
RTU 1 | 3/4" | 1 | D2
RTU 2 | 1" | 1.25 | D3
RTU 3 | 1-1/4" | 1.5 | D4
RTU 4 | 1-1/2" |  | D5
RTU 5 | 2" |  | D6
RTU 6 | 2-1/2" |  | D7
RTU 7 | 3" |  | D8
RTU 8 | 3-1/2" |  | D9
SLOC | 4"
DLOC
OMDC

## SYNEXIS
Customer Status
4941 | Active
539 | Active
2777 | Active
3184 | Active
2928 | Active
2209 | Active
4251 | Active
3303 | Active
3540 | Active
1724 | Active
2629 | Active
1293 | Active
1047 | Active
1826 | Active
9 | Active
4574 | Active
1414 | Active
418 | Active
2117 | Active
4628 | Active
1709 | Active
2813 | Active
4013 | Active
2292 | Active
2449 | Active
2984 | Active
1703 | Active
718 | Active
3642 | Active
3381 | Active
4006 | Active
3497 | Active
4175 | Active
2858 | Active
2821 | Active
4102 | Active
457 | Active
3192 | Active
1149 | Active
2829 | Active
1368 | Active
4279 | Active
3507 | Active
799 | Active
4325 | Active
1227 | Active
1976 | Active
3740 | Active
3778 | Active
3829 | Active
1763 | Active
1585 | Active
2913 | Active
3312 | Active
1130 | Active
1544 | Active
2869 | Active
4133 | Active
1086 | Active
1706 | Active
1601 | Active
3154 | Active
2981 | Active
1222 | Active
4324 | Active
2784 | Active
1951 | Active
2363 | Active
3180 | Active
3749 | Active
3146 | Active
2665 | Active
4081 | Active
1454 | Active
1449 | Active
3755 | Active
3693 | Active
592 | Active
1956 | Active
1048 | Active
92 | Active
3675 | Active
1639 | Active
2571 | Active
4566 | Active
717 | Active
792 | Active
4093 | Active
1085 | Active
4791 | Active
1980 | Active
3449 | Active
1814 | Active
1867 | Active
4028 | Active
3255 | Active
981 | Active
2500 | Active
4345 | Active
4335 | Active
1691 | Active
1183 | Active
1591 | Active
4159 | Active
791 | Active
1883 | Active
4451 | Active
859 | Active
1228 | Active
2415 | Active
528 | Active
2034 | Active
2918 | Active
2797 | Active
756 | Active
4695 | Active
3031 | Active
3511 | Active
745 | Active
1999 | Active
4215 | Active
2193 | Active
2425 | Active
2763 | Active
4103 | Active
562 | Active
1259 | Active
869 | Active
3309 | Active
2616 | Active
2436 | Active
1546 | Active
2825 | Active
3904 | Active
3664 | Active
2545 | Active
2942 | Active
4344 | Active
3334 | Active
2086 | Active
3571 | Active
3273 | Active
2664 | Active
1089 | Active
2884 | Active
2906 | Active
1210 | Active
1493 | Active
3592 | Active
2047 | Active
1463 | Active
2957 | Active
1769 | Active
2493 | Active
3072 | Active
2435 | Active
694 | Active
3060 | Active
2264 | Active
3288 | Active
2201 | Active
2551 | Active
3713 | Active
771 | Active
2103 | Active
4717 | Active
1682 | Active
3468 | Active
1111 | Active
242 | Active
2585 | Active
4072 | Active
2681 | Active
3529 | Active
3898 | Active
1977 | Active
1501 | Active
2483 | Active
1018 | Active
1986 | Active
3848 | Active
3422 | Active
2644 | Active
1825 | Active
2244 | Active
3825 | Active
3308 | Active
3972 | Active
3018 | Active
1390 | Active
1731 | Active
701 | Active
1072 | Active
2621 | Active
3619 | Active
3925 | Active
2849 | Active
3138 | Active
3032 | Active
2956 | Active
1125 | Active
2587 | Active
2931 | Active
3141 | Active
4000 | Active
4769 | Active
3366 | Active
4023 | Active
1649 | Active
1635 | Active
1284 | Active
3957 | Active
4473 | Active
2822 | Active
695 | Active
3632 | Active
3490 | Active
4063 | Active
1579 | Active
1805 | Active
1796 | Active
3810 | Active
4310 | Active
1098 | Active
1524 | Active
3212 | Active
643 | Active
777 | Active
2759 | Active
2470 | Active
1995 | Active
288 | Active
3077 | Active
3562 | Active
3489 | Active
1509 | Active
3795 | Active
1280 | Active
986 | Active
1445 | Active
358 | Active
3106 | Active
1942 | Active
1661 | Active
4621 | Active
3526 | Active
4073 | Active
3262 | Active
3343 | Active
4235 | Active
524 | Active
3423 | Active
1855 | Active
3037 | Active
1083 | Active
737 | Active
1772 | Active
3300 | Active
3790 | Active
3533 | Active
4139 | Active
3794 | Active
2289 | Active
3248 | Active
4323 | Active
4329 | Active
2698 | Active
8 | Active
930 | Active
2508 | Active
3901 | Active
3750 | Active
579 | Active
4480 | Active
2955 | Active
2024 | Active
2599 | Active
1170 | Active
2792 | Active
1431 | Active
1069 | Active
2820 | Inactive - Cancelled
2331 | Inactive - Cancelled
3667 | Inactive - Cancelled
4085 | Inactive - Cancelled
3823 | Inactive - Cancelled
3694 | Inactive - Cancelled
3295 | Inactive - Cancelled
3382 | Inactive - Cancelled
3809 | Inactive - Cancelled
2713 | Inactive - Cancelled
482 | Inactive - Cancelled
2456 | Inactive - Cancelled
3374 | Inactive - Cancelled
368 | Inactive - Cancelled
829 | Inactive - Cancelled
1704 | Inactive - Cancelled
2817 | Inactive - Cancelled
3791 | Inactive - Cancelled
1433 | Inactive - Cancelled
3840 | Inactive - Cancelled
231 | Inactive - Cancelled
3433 | Inactive - Cancelled
4496 | Inactive - Cancelled
430 | Inactive - Cancelled
4627 | Inactive - Cancelled
1385 | Inactive - Cancelled
3827 | Inactive - Cancelled
2407 | Inactive - Cancelled
1446 | Inactive - Cancelled
2066 | Inactive - Cancelled
4437 | Inactive - Cancelled
3432 | Inactive - Cancelled
2947 | Inactive - Cancelled
3189 | Inactive - Cancelled
3486 | Inactive - Cancelled
3769 | Inactive - Cancelled
4068 | Inactive - Cancelled
2050 | Inactive - Cancelled
4271 | Inactive - Cancelled
1764 | Inactive - Cancelled
4144 | Inactive - Cancelled
3748 | Inactive - Cancelled
3544 | Inactive - Cancelled
4457 | Inactive - Cancelled
1732 | Inactive - Cancelled
4264 | Inactive - Cancelled
2968 | Inactive - Cancelled
3239 | Inactive - Cancelled
2185 | Inactive - Cancelled
1031 | Inactive - Cancelled
3040 | Inactive - Cancelled
1540 | Inactive - Cancelled
3912 | Inactive - Cancelled
1647 | Inactive - Cancelled
2640 | Inactive - Cancelled
3431 | Inactive - Cancelled
3817 | Inactive - Cancelled
2788 | Inactive - Cancelled
2793 | Inactive - Cancelled
1827 | Inactive - Cancelled
2509 | Inactive - Cancelled
2367 | Inactive - Cancelled
3695 | Inactive - Cancelled
3440 | Inactive - Cancelled
2194 | Inactive - Cancelled
1103 | Inactive - Cancelled
1186 | Inactive - Cancelled
1815 | Inactive - Cancelled
4827 | Inactive - Cancelled
2501 | Inactive - Cancelled
1053 | Inactive - Cancelled
3307 | Inactive - Cancelled
3843 | Inactive - Cancelled
3424 | Inactive - Cancelled
1886 | Inactive - Cancelled
2131 | Inactive - Cancelled
4070 | Inactive - Cancelled
3688 | Inactive - Cancelled
662 | Inactive - Cancelled
2013 | Inactive - Cancelled
4402 | Inactive - Cancelled
3195 | Inactive - Cancelled
3372 | Inactive - Cancelled
3022 | Inactive - Cancelled
1014 | Inactive - Cancelled
3499 | Inactive - Cancelled
2891 | Inactive - Cancelled
3253 | Inactive - Cancelled
1982 | Inactive - Cancelled
2899 | Inactive - Cancelled
998 | Inactive - Cancelled
3808 | Inactive - Cancelled
3613 | Inactive - Cancelled
3020 | Inactive - Cancelled
361 | Inactive - Cancelled
4800 | Inactive - Cancelled
3410 | Inactive - Cancelled
57 | Inactive - Cancelled
3622 | Inactive - Cancelled
3578 | Inactive - Cancelled
2662 | Inactive - Cancelled
2320 | Inactive - Cancelled
1939 | Inactive - Cancelled
1895 | Inactive - Cancelled
3773 | Inactive - Cancelled
3685 | Inactive - Cancelled
4149 | Inactive - Cancelled
2000 | Inactive - Cancelled
3763 | Inactive - Non-Renewed
3662 | Inactive - Non-Renewed
2636 | Inactive - Non-Renewed
2141 | Inactive - Non-Renewed
1739 | Inactive - Non-Renewed
1139 | Inactive - Non-Renewed
3830 | Inactive - Non-Renewed
3700 | Inactive - Non-Renewed
1911 | Inactive - Non-Renewed
1223 | Inactive - Non-Renewed
732 | Inactive - Non-Renewed
2811 | Inactive - Non-Renewed
1481 | Inactive - Non-Renewed
1947 | Inactive - Non-Renewed
2856 | Inactive - Non-Renewed
2940 | Inactive - Non-Renewed
1157 | Inactive - Non-Renewed
1248 | Inactive - Non-Renewed
617 | Inactive - Non-Renewed
3056 | Inactive - Non-Renewed
2680 | Inactive - Non-Renewed
2554 | Inactive - Non-Renewed
4386 | Inactive - Non-Renewed
2688 | Inactive - Non-Renewed
2724 | Inactive - Non-Renewed
1489 | Inactive - Non-Renewed
1697 | Inactive - Non-Renewed
4040 | Inactive - Non-Renewed