## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3280 | 2900 | 2748 | 500 | 532 | 14.71% | 16.22%
RTU-2 | DINING | 3400 | 0 | 2400 | 0 | 1000 | 0 | 29.41% | #DIV/0!
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1277
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2464
EF-2 | RESTROOM | [12 empty] | 150 | 147
TOTALS |  | 6800 | 3280 | 5300 | 2748 | 1500 | 532 |  |  | 1300 | 1277 | 2550 | 2464 | 150 | 147
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2800 | 1809 |  | FRONT |  | -0.04 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2700 | 2611 |  | SIDE |  | -0.02 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | -802 |  | REAR |  | -0.02 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.026667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
RTU 2 NOT RUNNING. UNABLE TO BALANCE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250