## 2EP-2925
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE |  |  | RTU-1 | KITCHEN | 500 |  | 0 |  |  | 890 / 790 | 2 | 460 | 3 | 6 | 4 | 3 | 1.3333 | 1 | -25%
TRANE |  |  | RTU-2 | DINING | 1000 |  | 1000 |  |  |  | 1 |  |  | 4 | 3 | 2 | 0.75 | 0.5 | -33.33%
CAPTIVE-AIRE |  |  | MUA-1 | HOOD 1 | 1775 |  | 1500 |  |  |  | 1 |  |  | 4 | 3 | 2 | 0.75 | 0.5 | -33.33%
CAPTIVE-AIRE |  |  | EF-1 | HOOD 1 | 2925 | 0 | 2200 |  |  |  | 1 |  |  | 4 | 3 | 2 | 0.75 | 0.5 | -33.33%
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150 | [10 empty] | #DIV/0!
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3275 | 0 | 2500 | 0 |  | FRONT DOOR | 2.5833 | 0 | INITIAL
|  |  | TOTAL EXHAUST |  | 3075 | 150 | 2350 | 150 |  | BACK DOOR | 1.5 | 0 | FINAL
|  |  | NET AIRFLOW |  | 200 | -150 | 150 | -150 |  | AVERAGE | -41.94% | 0 | NET CHANGE

## 2EP-3200
STORE #: | #3098 | [22 empty] | Choose Yes or No:
CITY, STATE: | LOVELAND | OHIO | [21 empty] | Yes
HOOD TYPE: | 2 END PANEL - 171" HOOD LENGTH | [22 empty] | No
DATE: | 2023-05-12
TECH: | TYLER Y
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ078N12B2B5EAA2A1 | N1C7534764 | RTU-1 | KITCHEN | 500 | 149 | 0 | 0 |  | 1756 | 1756 | 722 | 722 | 1.5 | 210.9 | 210.9 | 3 | 5.2 | 2.99 | 2.95 | 1.0541 | 1.04 | -1.338%
YORK | ZJ090N18D2B5EAA2A1 | N1C7570553 | RTU-2 | DINING | 1000 | 0 | 1000 | 0 |  | 1755 | 1749 | 856 | 918 | 3 | 211.2 | 211.2 | 3 | 9.5 | 6.22 | 6.41 | 2.196 | 2.263 | 3.055%
CAPTIVE AIRE | A1-D.250-G10 | 2886821 | MUA-1 | HOOD 1 | 1775 | 1863 | 1500 | 1559 | No | 1768 | 1774 | 951 | 879 | 2 | 209.5 | 209.5 | 3 | 5.9 | 2.93 | 2.82 | 0.99322 | 0.95593 | -3.754%
CAPTIVE AIRE | NCA24HPFA | 2886821 | EF-1 | HOOD 1 | 2925 | 2693 | 2200 | 2274 | Yes | 1759 | 1773 | 801 | 714 | 2 | 210.2 | 210.2 | 3 | 5.9 | 3.65 | 3 | 1.2373 | 1.0169 | -17.81%
| RR FAN RUNNING? | No | EF-2 | RESTROOM | 150 | 0 | 150 | 0
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3275 | 2012 | 2500 | 1559 |  | FRONT DOOR |  | -0.022 |  |  | INITIAL | 5.4806 | 2012
|  |  | TOTAL EXHAUST |  | 3075 | 2693 | 2350 | 2274 |  | BACK DOOR |  | -0.02 |  |  | FINAL | 5.2759 | 3833
|  |  | NET AIRFLOW |  | 200 | -681 | 150 | -715 |  | AVERAGE |  | -0.021 |  |  | ∆ | 0.20465 | 1821