## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 820 | 350 | 364
RTU-2 | SALES | 800 | 834 | 350 | 385
RTU-3 | BOH/KITCHEN | 800 | 866 | 350 | 369
EF-1 | RR/JANITOR |  |  |  |  | 750 | 802 | 750 | 802
EF-2 | COMBI-OVEN |  |  |  |  | 150 | 267 | 150 | 267
EF-3 | HOOD |  |  |  |  | 1350 | 1460 | 0 | 0
TOTALS |  | 2400 | 2520 | 1050 | 1118 | 2250 | 2529 | 900 | 1069
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2520 |  |  | FRONT |  | 0.002 |  | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 2250 | 2529 |  |  | SIDE |  | 0.001
NET AIRFLOW |  | 150 | -9 |  |  | REAR |  |  |  | TRUE
[6 empty] | AVERAGE |  | 0.0015
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 1118 |  |  | FRONT |  | 0.004
TOTAL EXHAUST |  | 900 | 1069 |  |  | SIDE |  | 0.003
NET AIRFLOW |  | 150 | 49 |  |  | REAR
[6 empty] | AVERAGE |  | 0.0035
NOTES:
Building is barely neutral w/ Hood On. Recommend fixing exhaust design so hood fan can be turned back down to design (instead of ~10% over), and installing combi-oven exhaust with TAB present so it can be properly balanced - or make the exhaust accessible in some other way. OA left on 'high side' to make-up for higher exhaust. Rear door air curtain could not be shut off as usual without pinching monitor tube, accurate pressure reading not possible.