## RTU-1N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-1N Area: FLOOR 1 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF6040VN7 |  | Model Number | SAHLF6040VN7
Serial Number | C22A00039 |  | Serial Number | C22A00039
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 254T |  | Motor MFG / Frame | MARATHON / 213T
Horsepower / RPM | 7.5 X2 / 1180 |  | Horsepower / RPM | 7.5 / 1766
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 11.4 / 1.15 |  | Rated Amperage / SF | 9.9 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 18235 |  | Total CFM | 16000
OA CFM
Fan RPM | 1453 |  | Fan RPM | 693
VFD Speed |  |  | Motor HZ
RL Voltage | 460 |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 12.73 |  | Motor B.H.P. | 4.23
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.40 |  | Total SP
DX Coil P.D. | 0.90
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-1S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-1S Area: FLOOR 1 SOUTH
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040VN8 |  | Model Number | SAHLF7040VN8
Serial Number | C22B01758 |  | Serial Number | C22B01758
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | MARATHON / 213T
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 7.5 / 1766
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 9.9 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 20585 |  | Total CFM | 18000
OA CFM
Fan RPM | 1299 |  | Fan RPM | 766
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 15.03 |  | Motor B.H.P. | 5.63
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P.
Total SP |  |  | Discharge S.P.
DX Coil P.D. | 3.618" |  | Total SP
Pre Filters P.D.
System Set Point
Total ESP

## RTU-2N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-2N Area: FLOOR 2 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00041 |  | Serial Number | C22A00041
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 254T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 15 X2 / 1765 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22405 |  | Total CFM | 17000
OA CFM
Fan RPM | 1702 |  | Fan RPM | 482
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 15.03 |  | Motor B.H.P. | 5.63
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.69" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-2S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-2S Area: FLOOR 2 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00042 |  | Serial Number | C22A00042
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 254T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 15 X2 / 1765 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22115 |  | Total CFM | 17000
OA CFM
Fan RPM | 1685 |  | Fan RPM | 482
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 20.62 |  | Motor B.H.P. | 3.95
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.660" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-3N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-3N Area: FLOOR 3 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00043 |  | Serial Number | C22A00043
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21325 |  | Total CFM | 18000
OA CFM
Fan RPM | 1366 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.48 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.496" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-3S
National TAB
Project: IBP 18 - SHELL
System: AHU
Asset: RTU-3S Area: FLOOR 3 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00044 |  | Serial Number | C22A00044
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21115 |  | Total CFM | 18000
OA CFM
Fan RPM | 1396 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 18.56 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.570" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-4N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-4N Area: FLOOR 4 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00045 |  | Serial Number | C22A00045
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21050 |  | Total CFM | 18000
OA CFM
Fan RPM | 1356 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.12 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.470" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-4S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-4S Area: FLOOR 4 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00046 |  | Serial Number | C22A00046
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22180 |  | Total CFM | 18000
OA CFM
Fan RPM | 1398 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 18.65 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.575" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-5N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-5N Area: FLOOR 5 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7540V45 |  | Model Number | SAHLF7540V45
Serial Number | C22A00047 |  | Serial Number | C22A00047
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 284T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 15 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 20.5 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 26860 |  | Total CFM | 18000
OA CFM
Fan RPM | 1554 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.12 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.747" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-5S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-5S Area: FLOOR 5 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7540V45 |  | Model Number | SAHLF7540V45
Serial Number | C22A00048 |  | Serial Number | C22A00048
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 284T |  | Motor MFG / Frame | CENTURY / 184 T
Horsepower / RPM | 15 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 20.5 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 26605 |  | Total CFM | 18000
OA CFM
Fan RPM | 1543 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 24.10 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.724" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP