## RTU-1N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-1N Area: FLOOR 1 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF6040VN7 |  | Model Number | SAHLF6040VN7
Serial Number | C22A00039 |  | Serial Number | C22A00039
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 254T |  | Motor MFG / Frame | MARATHON / 213T
Horsepower / RPM | 7.5 X2 / 1180 |  | Horsepower / RPM | 7.5 / 1766
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 11.4 / 1.15 |  | Rated Amperage / SF | 9.9 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 18235 |  | Total CFM | 16000
OA CFM
Fan RPM | 1453 |  | Fan RPM | 693
VFD Speed |  |  | Motor HZ
RL Voltage | 460 |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 12.73 |  | Motor B.H.P. | 4.23
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.40 |  | Total SP
DX Coil P.D. | 0.90
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-1N VAVs
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-1N-1 | FLR 1 NORTH RR | CV-1N-15 | SERIES | 8 | 420 | 417 | 100 | 99 | 420 | 417 | 860
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-1N-1 | FLR 1 NORTH CORE | VAV-1N-14 | COOL | 8 | 650 | 654 | 100 | 103 | N/A | N/A | 774
VRH-1N-1 | FLR 1 LOBBY | VRH-1N-16 | HEAT | 8 | 700 | 706 | 210 | 203 | 210 | 203 | 834.6
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY

## RTU-1N GRD's
National TAB
Project:
RTU-1N GRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C1N1-1 | FLR 1 NORTH RR | D(PL) | 8 | 210 | 233 | 204 | 0.97143
C1N1-2 | FLR 1 NORTH RR | D(PL) | 8 | 210 | 217 | 213 | 1.0143
CV-1N-1 |  |  |  | 420 | 450 | 417 | 0.99286
V1N1-1 | FLR 1 NORTH CORE | C | 12X6 | 150 | 151 | 147 | 0.98
V1N1-2 | FLR 1 NORTH CORE | C | 20X10 | 500 | 437 | 507 | 1.014
VAV-1N-1 |  |  |  | 650 | 588 | 654 | 1.0062
H1N1-1 | FLR 1 LOBBY | B | 8 | 105 | 84 | 101 | 0.9619
H1N1-2 | FLR 1 LOBBY | B | 8 | 105 | 97 | 110 | 1.0476
H1N1-3 | FLR 1 LOBBY | A | 6 | 70 | 57 | 72 | 1.0286
H1N1-4 | FLR 1 LOBBY | D(PL) | 8 | 210 | 253 | 214 | 1.019
H1N1-5 | FLR 1 LOBBY | D(PL) | 8 | 210 | 230 | 209 | 0.99524
VRH-1N-1 |  |  |  | 700 | 721 | 706 | 1.0086

## RTU-1S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-1S Area: FLOOR 1 SOUTH
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040VN8 |  | Model Number | SAHLF7040VN8
Serial Number | C22B01758 |  | Serial Number | C22B01758
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | MARATHON / 213T
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 7.5 / 1766
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 9.9 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 20585 |  | Total CFM | 18000
OA CFM
Fan RPM | 1299 |  | Fan RPM | 766
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 15.03 |  | Motor B.H.P. | 5.63
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P.
Total SP |  |  | Discharge S.P.
DX Coil P.D. | 3.618" |  | Total SP
Pre Filters P.D.
System Set Point
Total ESP

## RTU-1S VAVs
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-1S-1 | FLR1 SOUTH RR | CV-1S-11 | SERIES | 6 | 300 | 302 | 100 | 98 | 300 | 305 | 581.9
Asset: Parallel Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Min CFM | Design Fan + Heat CFM | Actual Fan + Heat CFM | Ak (max)
FPB-1S-1 | FLR 1 FCS, FARS | FPB-1S-13 | PARALLEL | 8 | 500 | 503 | 50 | 48 | 400 | 416 | 737.9
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-1S-1 | FLR 1 SOUTH CORE | VAV-1S-10 | COOL | 8 | 650 | 646 | 100 | 104 | N/A | N/A | 883.9
VAV-1S-2 | FLR 1 SOUTH OFC | VAV-1S-12 | COOL | 10 | 1150 | 1144 | 100 | 101 | N/A | N/A | 1218.1
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY
Note on J13: NTAB: Fan PLUS Heat CFM
Note on C19: NTAB: BILLINGSLEY ONLY

## RTU-1S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-1S GRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C1S1-1 | FLR 1 SOUTH RR | D(PL) | 8 | 150 | 133 | 148 | 0.98667
C1S1-2 | FLR 1 SOUTH RR | D(PL) | 8 | 150 | 148 | 154 | 1.0267
CV-1S-1 |  |  |  | 300 | 281 | 302 | 1.0067
F1S1-1 | FLR 1 FCS, FARS | C | 12X6 | 150 | 130 | 156 | 1.04
F1S1-2 | FLR 1 FCS, FARS | C | 14X8 | 350 | 294 | 347 | 0.99143
FPB-1S-1 |  |  |  | 500 | 424 | 503 | 1.006
V1S1-1 | FLR 1 SOUTH CORE | C | 20X10 | 500 | 425 | 493 | 0.986
V1S1-2 | FLR 1 SOUTH CORE | C | 12X6 | 150 | 233 | 153 | 1.02
VAV-1S-1 |  |  |  | 650 | 658 | 646 | 0.99385
V1S2-1 | FLR 1 SOUTH OFC | C | 12X6 | 175 | 118 | 164 | 0.93714
V1S2-2 | FLR 1 SOUTH OFC | C | 12X6 | 245 | 220 | 232 | 0.94694
V1S2-3 | FLR 1 SOUTH OFC | C | 20X10 | 730 | 823 | 748 | 1.0247
VAV-1S-2 |  |  |  | 1150 | 1161 | 1144 | 0.99478
Test Date:

## RTU-2N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-2N Area: FLOOR 2 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00041 |  | Serial Number | C22A00041
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 254T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 15 X2 / 1765 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22405 |  | Total CFM | 17000
OA CFM
Fan RPM | 1702 |  | Fan RPM | 482
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 15.03 |  | Motor B.H.P. | 5.63
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.69" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-2N VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CVN-2N-1 | FLR 2 NORTH RR | CV-2N-22 | SERIES | 8 | 300 | 305 | 100 | 99 | 300 | 305 | 908
Asset: Parallel Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Min CFM | Design Fan + Heat CFM | Actual Fan + Heat CFM | Ak (max)
FPB-2N-1 | WEST LOBBY EXT | FPB-2N-24 | PARALLEL | 14 | 2400 | 2376 | 240 | 244 | 1850 | 1874 | 2189.9
FPB-2N-2 | WEST LOBBY INT | FPB-2N-23 | PARALLEL | 10 | 1000 | 988 | 100 | 104 | 600 | 598 | 1168.4
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-2N-1 | FLR 2 NORTH CORE | VAV-2N-25 | COOL | 8 | 650 | 659 | 100 | 102 | N/A | N/A | 732.6
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY
Note on J13: NTAB: Fan PLUS Heat CFM
Note on C20: NTAB: BILLINGSLEY ONLY

## RTU-2N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-2N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C2N1-1 | FLR 2 NORTH RR | D(PL) | 8 | 150 | 176 | 154 | 1.0267
C2N1-2 | FLR 2 NORTH RR | D(PL) | 8 | 150 | 142 | 151 | 1.0067
CV-2N-1 |  |  |  | 300 | 318 | 305 | 1.0167
F2N1-1 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
F2N1-2 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
F2N1-3 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0 | UNABLE TO ACCESS GRILLES. UNIT BALANCED IN TOTAL.
F2N1-4 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
F2N1-5 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
F2N1-6 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
F2N1-7 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
F2N1-8 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1 |  |  |  | 2400 | 0 | 0 | 0
F2N2-1 | WEST LOBBY INT | D(PL) | 12 | 250 | 81 | 238 | 0.952
F2N2-2 | WEST LOBBY INT | D(PL) | 12 | 250 | 104 | 243 | 0.972
F2N2-3 | WEST LOBBY INT | D(PL) | 12 | 250 | 309 | 267 | 1.068
F2N2-4 | WEST LOBBY INT | D(PL) | 12 | 250 | 358 | 240 | 0.96
FPB-2N-2 |  |  |  | 1000 | 852 | 988 | 0.988
V2N1-1 | FLR 2 NORTH CORE | C | 12X6 | 150 | 59 | 150 | 1
V2N1-2 | FLR 2 NORTH CORE | C | 20X10 | 500 | 458 | 509 | 1.018
VAV-2N-1 |  |  |  | 650 | 517 | 659 | 1.0138
Test Date:

## RTU-2S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-2S Area: FLOOR 2 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00042 |  | Serial Number | C22A00042
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 254T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 15 X2 / 1765 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22115 |  | Total CFM | 17000
OA CFM
Fan RPM | 1685 |  | Fan RPM | 482
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 20.62 |  | Motor B.H.P. | 3.95
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.660" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-2S VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-2S-1 | FLR 2 SOUTH RR | CV-2S-18 | SERIES | 6 | 300 | 297 | 100 | 102 | 300 | 304 | 600.8
Asset: Parallel Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Min CFM | Design Fan + Heat CFM | Actual Fan + Heat CFM | Ak (max)
FPB-2S-1 | EAST LOBBY | FPB-2S-20 | PARALLEL | 12 | 2000 | 1995 | 200 | 192 | 1540 | 1562 | 1974.9
FPB-2S-2 | EAST VEST | FPB-2S-19 | PARALLEL | 8 | 600 | 607 | 60 | 62 | 460 | 475 | 857.1
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-2S-1 | FLR 2 SOUTH CORE | VAV-2S-19 | COOL | 8 | 650 | 659 | 100 | 102 | N/A | N/A | 671.2
VRH-2S-1 | FLR 2 LOBBY | VRH-2S-21 | HEAT | 6 | 300 | 302 | 100 | 99 | 100 | 99 | 552.1
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY
Note on J13: NTAB: Fan PLUS Heat CFM
Note on C20: NTAB: BILLINGSLEY ONLY

## RTU-2S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-2S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C2S1-1 | FLR 2 SOUTH RR | D(PL) | 8 | 150 | 156 | 147 | 0.98
C2S1-2 | FLR 2 SOUTH RR | D(PL) | 8 | 150 | 167 | 157 | 1.0467
CV-2S-1 |  |  |  | 300 | 323 | 304 | 1.0133
F2S1-1 | EAST LOBBY | D(PL) | 12 | 500 | 298 | 511 | 1.022
F2S1-2 | EAST LOBBY | D(PL) | 12 | 500 | 341 | 519 | 1.038
F2S1-3 | EAST LOBBY | D(PL) | 12 | 500 | 620 | 489 | 0.978
F2S1-4 | EAST LOBBY | D(PL) | 12 | 500 | 684 | 476 | 0.952
FPB-2S-1 |  |  |  | 2000 | 1943 | 1995 | 0.9975
F2S2-1 | EAST VEST | D(PL) | 12 | 300 | 322 | 304 | 1.0133
F2S2-2 | EAST VEST | D(PL) | 12 | 300 | 324 | 303 | 1.01
FPB-2S-2 |  |  |  | 600 | 646 | 607 | 1.0117
V2S1-1 | FLR 2 SOUTH CORE | C | 20X10 | 500 | 324 | 517 | 1.034
V2S1-2 | FLR 2 SOUTH CORE | C | 12X6 | 150 | 151 | 142 | 0.94667
VAV-2S-1 |  |  |  | 650 | 475 | 659 | 1.0138
H2S1-1 | FLR 2 LOBBY | B | 8 | 150 | 179 | 154 | 1.0267
H2S1-2 | FLR 2 LOBBY | B | 8 | 150 | 143 | 148 | 0.98667
VRH-2S-1 |  |  |  | 300 | 322 | 302 | 1.0067
Test Date:

## RTU-3N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-3N Area: FLOOR 3 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00043 |  | Serial Number | C22A00043
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21325 |  | Total CFM | 18000
OA CFM
Fan RPM | 1366 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.48 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.496" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-3N VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-3S-1 | FLR 3 NORTH RR | CV-3N-28 | SERIES | 8 | 300 | 303 | 100 | 102 | 300 | 304 | 741.9
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-3N-1 | FLR3 NORTH CORE | VAV-3N-29 | COOL | 8 | 650 | 655 | 100 | 104 | N/A | N/A | 663.9
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY

## RTU-3N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-3N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C3N1-1 | FLR 3 NORTH RR | D(PL) | 8 | 150 | 134 | 154 | 1.0267
C3N1-2 | FLR 3 NORTH RR | D(PL) | 8 | 150 | 147 | 150 | 1
CV-3N-1 |  |  |  | 300 | 281 | 304 | 1.0133
V3N1-1 | FLR 3 NORTH CORE | C | 12X6 | 150 | 139 | 150 | 1
V3N1-2 | FLR 3 NORTH CORE | C | 20X10 | 500 | 386 | 505 | 1.01
VAV-3N-1 |  |  |  | 650 | 525 | 655 | 1.0077
Test Date:

## RTU-3S
National TAB
Project: IBP 18 - SHELL
System: AHU
Asset: RTU-3S Area: FLOOR 3 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00044 |  | Serial Number | C22A00044
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21115 |  | Total CFM | 18000
OA CFM
Fan RPM | 1396 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 18.56 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.570" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-3S VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-3S-1 | FLR 3 SOUTH RR | CV-3S-26 | SERIES | 6 | 300 | 306 | 100 | 102 | 300 | 307 | 642.9
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-3S-1 | FLR3 SOUTH CORE | VAV-3S-27 | COOL | 8 | 650 | 658 | 100 | 98 | N/A | N/A | 688.1
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY

## RTU-3S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-3S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C3S1-1 | FLR 3 SOUTH RR | D(PL) | 8 | 150 | 129 | 152 | 1.0133
C3S1-2 | FLR 3 SOUTH RR | D(PL) | 8 | 150 | 118 | 154 | 1.0267
CV-3S-1 |  |  |  | 300 | 247 | 306 | 1.02
V3S1-1 | FLR 3 SOUTH CORE | C | 20X10 | 500 | 370 | 496 | 0.992
V3S1-2 | FLR 3 SOUTH CORE | C | 12X6 | 150 | 165 | 162 | 1.08
VAV-3S-1 |  |  |  | 650 | 535 | 658 | 1.0123
Test Date:

## RTU-4N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-4N Area: FLOOR 4 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00045 |  | Serial Number | C22A00045
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21050 |  | Total CFM | 18000
OA CFM
Fan RPM | 1356 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.12 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.470" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-4N VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-4N-1 | FLR 4 NORTH RR | CV-4N-32 | SERIES | 8 | 300 | 299 | 100 | 102 | 300 | 309 | 882.2
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-4N-1 | FLR 4 NORTH CORE | VAV-4N-33 | COOL | 8 | 650 | 644 | 100 | 103 | N/A | N/A | 768
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY

## RTU-4N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-4N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C4N1-1 | FLR 4 NORTH RR | D(PL) | 8 | 150 | 131 | 145 | 0.96667
C4N1-2 | FLR 4 NORTH RR | D(PL) | 8 | 150 | 187 | 154 | 1.0267
CV-4N-1 |  |  |  | 300 | 318 | 299 | 0.99667
V4N1-1 | FLR 4 NORTH CORE | C | 12X6 | 150 | 162 | 147 | 0.98
V4N1-2 | FLR 4 NORTH CORE | C | 20X10 | 500 | 423 | 497 | 0.994
VAV-4N-1 |  |  |  | 650 | 585 | 644 | 0.99077
Test Date:

## RTU-4S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-4S Area: FLOOR 4 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040V45 |  | Model Number | SAHLF7040V45
Serial Number | C22A00046 |  | Serial Number | C22A00046
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 256T |  | Motor MFG / Frame | CENTURY
Horsepower / RPM | 10 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.3 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22180 |  | Total CFM | 18000
OA CFM
Fan RPM | 1398 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 18.65 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.575" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-4S VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-4S-1 | FLR 4 SOUTH RR | CV-4S-30 | SERIES | 8 | 300 | 304 | 100 | 105 | 300 | 314 | 664.4
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-4S-1 | FLR 4 SOUTH CORE | VAV-4S-31 | COOL | 8 | 650 | 645 | 100 | 104 | N/A | N/A | 781.1
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY

## RTU-4S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-4S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C4S1-1 | FLR 4 SOUTH RR | D(PL) | 8 | 150 | 189 | 158 | 1.0533
C4S1-2 | FLR 4 SOUTH RR | D(PL) | 8 | 150 | 207 | 146 | 0.97333
CV-4S-1 |  |  |  | 300 | 396 | 304 | 1.0133
V4S1-1 | FLR4 SOUTH CORE | C | 20X10 | 500 | 444 | 488 | 0.976
V4S1-2 | FLR4 SOUTH CORE | C | 12X6 | 150 | 144 | 157 | 1.0467
VAV-4S-1 |  |  |  | 650 | 588 | 645 | 0.99231
Test Date:

## RTU-5N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-5N Area: FLOOR 5 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7540V45 |  | Model Number | SAHLF7540V45
Serial Number | C22A00047 |  | Serial Number | C22A00047
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 284T |  | Motor MFG / Frame | CENTURY / 184T
Horsepower / RPM | 15 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 20.5 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 26860 |  | Total CFM | 18000
OA CFM
Fan RPM | 1554 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.12 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.747" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-5N VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Fan CFM | Ak (max)
CV-5N-1 | FLR 5 NORTH RR | CV-5N-36 | SERIES | 8 | 300 | 307 | 100 | 104 | 300 | 302 | 626.2
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VRH-5N-1 | FLR 5 NORTH CORE | VRH-5N-37 | HEAT | 8 | 650 | 654 | 100 | 104 | 200 | 206 | 858.2
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY

## RTU-5N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-5N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C5N1-1 | FLR 5 NORTH RR | D(PL) | 8 | 150 | 133 | 148 | 0.98667
C5N1-2 | FLR 5 NORTH RR | D(PL) | 8 | 150 | 96 | 159 | 1.06
CV-5N-1 |  |  |  | 300 | 229 | 307 | 1.0233
H5N1-1 | FLR 5 NORTH CORE | C | 12X6 | 150 | 175 | 162 | 1.08
H5N1-2 | FLR 5 NORTH CORE | C | 20X10 | 500 | 501 | 492 | 0.984
VRH-5N-1 |  |  |  | 650 | 676 | 654 | 1.0062
Test Date:

## RTU-5S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-5S Area: FLOOR 5 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7540V45 |  | Model Number | SAHLF7540V45
Serial Number | C22A00048 |  | Serial Number | C22A00048
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2"
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR / 284T |  | Motor MFG / Frame | CENTURY / 184 T
Horsepower / RPM | 15 X2 / 1180 |  | Horsepower / RPM | 5 / 1755
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 20.5 / 1.15 |  | Rated Amperage / SF | 6.2 / 1.15
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 26605 |  | Total CFM | 18000
OA CFM
Fan RPM | 1543 |  | Fan RPM | 487
VFD Speed |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 24.10 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.724" |  | Total SP
DX Coil P.D.
Pre Filters P.D.
System Set Point
Total ESP |  |  | Total ESP

## RTU-5S VAV's
National TAB
Project: IBP 18 - SHELL
Address: 6275 Plano Parkway Plano, TX
Asset: Series Fan Powered Boxes
Asset | Area Served | Address | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Fan CFM | Ak (max)
CV-5S-1 | FLR 5 SOUTH RR | CV-5S-343 | SERIES | 6 | 300 | 303 | 100 | 102 | 300 | 307 | 335.7
Asset: Single Duct VAV's
Asset | Area Served | Address | Type | Size | Design Pri Max CFM | Actual Pri Max CFM | Design Pri Min CFM | Actual Pri Min CFM | Design Fan CFM | Actual Heat CFM | Ak (max)
VRH-5S-1 | FLR 5 SOUTH CORE | VRH-5S-35 | HEAT | 8 | 650 | 658 | 100 | 98 | 200 | 205 | 886.9
Note on C7: NTAB: BILLINGSLEY ONLY
Note on C13: NTAB: BILLINGSLEY ONLY

## RTU-5S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-5S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C5S1-1 | FLR 5 SOUTH RR | D(PL) | 8 | 150 | 119 | 146 | 0.97333
C5S1-2 | FLR 5 SOUTH RR | D(PL) | 8 | 150 | 93 | 157 | 1.0467
CV-5S-1 |  |  |  | 300 | 212 | 303 | 1.01
H5S1-1 | FLR 5 SOUTH CORE | C | 20X10 | 500 | 507 | 498 | 0.996
H5S1-2 | FLR 5 SOUTH CORE | C | 12X6 | 150 | 195 | 160 | 1.0667
VRH-5S-1 |  |  |  | 650 | 702 | 658 | 1.0123
Test Date:

## FCU-1
National TAB
Project:
Address:
Asset: FCU-1 |  | Area: 110
Unit Data |  |  |  |  | Test Data
MFG | MITSUBISHI ELECTRIC |  |  |  |  | Design | Actual
Model Num | TPEADA0181AA70A |  |  |  | SA CFM | 620
Serial Num | 1YR0079030P904 |  |  |  | Fan Speed
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP
Voltage (rated) | 208
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F1-1 | 110 | A | 10 | 320 |  |  | 0
F1-2 | 110 | A | 10 | 300 |  |  | 0
|  |  |  | 620 |  | 0 | 0

## EF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: EF-1 |  | Area: CORE NORTH RR/JAN
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size | 4.25
Model Num |  | USF-20-3-B1-00-01-01 |  |  | Motor Bore Size | 0.875
Serial Num |  | 20091822 |  |  | Fan Sheave Size | 7.25
Type |  | CRE UTILITY |  |  | Fan Bore Size | 1.1875
[5 empty] | Belt CL Distance | 17
Motor Data |  |  |  |  | No of Belts | 2
Motor MFG |  | WEG |  |  | Belt Size | AP50
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 3050 | 3251
Voltage (rated) |  | 460 |  |  | Fan RPM | 1004 | 1021
Amperage (rated) |  | 2.69 |  |  | RL Voltage |  | 496/497/496
Service Factor |  | 1.15 |  |  | RL Amperage |  | 1.9/1.9/1.9
[5 empty] | Suction ESP |  | -0.92
[5 empty] | Total ESP | 1 | 0.92
[5 empty] | Brake Horse Power | 0.9 | 1.41
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E1-1 | FLR 1 N RR | E | 10 | 280 |  | [1]
E1-2 | FLR 1 N RR | E | 10 | 280 |  | [1]
E1-3 | FLR 1 N JAN | H | 12X6 | 50 |  | [1]
E1-4 | FLR 2 N RR | E | 10 | 280 |  | 294 | 1.05
E1-5 | FLR 2 N RR | E | 10 | 280 |  | 276 | 0.98571
E1-6 | FLR 2 N JAN | H | 12X6 | 50 |  | 53 | 1.06
E1-7 | FLR 3 N RR | E | 10 | 280 |  | 274 | 0.97857
E1-8 | FLR 3 N RR | E | 10 | 280 |  | 286 | 1.0214
E1-9 | FLR 3 N JAN | H | 12X6 | 50 |  | 51 | 1.02
E1-10 | FLR 4 N RR | E | 10 | 280 |  | 288 | 1.0286
E1-11 | FLR 4 N RR | E | 10 | 280 |  | 279 | 0.99643
E1-12 | FLR 4 N JAN | H | 12X6 | 50 |  | 54 | 1.08
E1-13 | FLR 5 N RR | E | 10 | 280 |  | 290 | 1.0357
E1-14 | FLR 5 N RR | E | 10 | 280 |  | 284 | 1.0143
E1-15 | FLR 5 N JAN | H | 12X6 | 50 |  | 52 | 1.04
|  |  |  | 3050 | 3608 | 3251 | 1.0659
Test Date: | 2023-02-13 |  |  |  | GRILLES AND DAMPERS TO E1-1 THROUGH E1-3 ARE INACESSIBLE.
TOTAL TRAVERSE AFTER DAMPERING ADDS TO 3251. UNABLE TO READ FIRST 3 GRILLES.
VALUE IN CFM(1) COLUMN IS A TOTAL TRAVERSE READING BEFORE DAMPERING.
-

## EF-2
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: EF-2 |  | Area: CORE SOUTH RR/JAN
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size | 4.25
Model Num |  | USF-20-3-B1-00-01-01 |  |  | Motor Bore Size | 0.875
Serial Num |  | 20091824 |  |  | Fan Sheave Size | 8.125
Type |  | CRE UTILITY |  |  | Fan Bore Size | 1.1875
[5 empty] | Belt CL Distance | 17.25
Motor Data |  |  |  |  | No of Belts | 2
Motor MFG |  | WEG |  |  | Belt Size | AP52
Frame |  | 143/5T
Horsepower |  | 1.5 |  |  | Test Data
Motor Rpm |  | 1760 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2350 | 2467
Voltage (rated) |  | 460 |  |  | Fan RPM | 902 | 894
Amperage (rated) |  | 2.07 |  |  | RL Voltage |  | 496/497/496
Service Factor |  | 1.15 |  |  | RL Amperage |  | 1.5/1.6/1.6
[5 empty] | Suction ESP |  | -0.87
[5 empty] | Total ESP | 1 | 0.87
[5 empty] | Brake Horse Power | 0.6 | 1.14
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E2-1 | FLR 1 S JAN | H | 12X6 | 50 |  | 53 | 1.06
E2-2 | FLR 1 S RR | E | 8 | 210 |  | 224 | 1.0667
E2-3 | FLR 1 S RR | E | 8 | 210 |  | 219 | 1.0429
E2-4 | FLR 2 S JAN | H | 12X6 | 50 |  | 53 | 1.06
E2-5 | FLR 2 S RR | E | 8 | 210 |  | 214 | 1.019
E2-6 | FLR 2 S RR | E | 8 | 210 |  | 215 | 1.0238
E2-7 | FLR 3 S JAN | H | 12X6 | 50 |  | 54 | 1.08
E2-8 | FLR 3 S RR | E | 8 | 210 |  | 223 | 1.0619
E2-9 | FLR 3 S RR | E | 8 | 210 |  | 220 | 1.0476
E2-10 | FLR 4 S JAN | H | 12X6 | 50 |  | 52 | 1.04
E2-11 | FLR 4 S RR | E | 8 | 210 |  | 219 | 1.0429
E2-12 | FLR 4 S RR | E | 8 | 210 |  | 223 | 1.0619
E2-13 | FLR 5 S JAN | H | 12X6 | 50 |  | 53 | 1.06
E2-14 | FLR 5 S RR | E | 8 | 210 |  | 224 | 1.0667
E2-15 | FLR 5 S RR | E | 8 | 210 |  | 221 | 1.0524
|  |  |  | 2350 | 2886 | 2467 | 1.0498
Test Date: | 2023-02-13
VALUE IN CFM(1) COLUMN IS A TOTAL TRAVERSE READING BEFORE DAMPERING.
-

## SEF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: SEF-1 |  | Area: SMOKE REMOVE NORTH
Unit Data |  |  |  |  | Drive Data
MFG |  |  |  |  | Motor Sheave Size
Model Num |  |  |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 20 |  |  | Test Data
Motor Rpm | [5 empty] | Design | Actual
Phase |  | 3 |  |  | CFM | 26000
Voltage (rated) |  | 460 |  |  | Fan RPM | 659
Amperage (rated) |  |  |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.5
[5 empty] | Brake Horse Power | 14.4
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
-

## SEF-2
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: SEF-2 |  | Area: SMOKE REMOVE SOUTH
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-44-3-B4-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091834 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 20 |  |  | Test Data
Motor Rpm | [5 empty] | Design | Actual
Phase |  | 3 |  |  | CFM | 26000
Voltage (rated) |  | 460 |  |  | Fan RPM | 659
Amperage (rated) |  |  |  |  | RL Voltage
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.5
[5 empty] | Brake Horse Power | 14.4
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
-

## EPF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: EPF-1 |  | Area: ELEVATOR HOISTWAY PRESSURIZATION
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-36-5-B4-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091826 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 286T
Horsepower |  | 25 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 22500
Voltage (rated) |  | 460 |  |  | Fan RPM | 1106
Amperage (rated) |  | 34 |  |  | RL Voltage | 460
Service Factor |  |  |  |  | RL Amperage | 34
Suction ESP
[5 empty] | Total ESP | 1.581
[5 empty] | Brake Horse Power | 17.3
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
-

## SPF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: SPF-1 |  | Area: STAIRWELL PRESSURIZATION - STAIR 3
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size | 4
Model Num |  | USF-18-3-B1-00-01-01 |  |  | Motor Bore Size | 0.875
Serial Num |  | 20091838 |  |  | Fan Sheave Size | 5.875
Type |  | UTILITY |  |  | Fan Bore Size | 1.125
[5 empty] | Belt CL Distance | 15.25
Motor Data |  |  |  |  | No of Belts | 2
Motor MFG |  | WEG |  |  | Belt Size | A44
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2800
Voltage (rated) |  | 460 |  |  | Fan RPM | 1168
Amperage (rated) |  | 2.69 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.324
[5 empty] | Brake Horse Power | 0.9
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
-

## SPF-2
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: SPF-2 |  | Area: STAIRWELL PRESSURIZATION - STAIR 2
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-18-3-B1-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091849 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | WEG |  |  | Belt Size
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2800
Voltage (rated) |  | 460 |  |  | Fan RPM | 1168
Amperage (rated) |  | 2.69 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.324
[5 empty] | Brake Horse Power | 0.9
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
-

## SPF-3
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: SPF-3 |  | Area: STAIRWELL PRESSURIZATION - STAIR 1
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-18-3-B1-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091852 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | WEG |  |  | Belt Size
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 3200
Voltage (rated) |  | 460 |  |  | Fan RPM | 1261
Amperage (rated) |  | 2.69 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.423
[5 empty] | Brake Horse Power | 0.9
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Test Date:
-

## SGRD - Blank
National TAB
Project: IBP 18 - SHELL
SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Test Date: