## RTU-1N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-1N Area: FLOOR 1 NORTH
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF6040VN7 CLFD8001B0CE 0V00000RT0M8 600 |  | Model Number
Serial Number | C22A00039 |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 15 / 1500 |  | Horsepower / RPM | 7.5 / 700
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 18235 |  | Total CFM | 16000
Fan RPM | 1453 |  | Fan RPM | 693
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 12.73 |  | Motor B.H.P. | 4.23
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.402" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-1N VAVs
National TAB
Project: IBP XVIII WITH RTU'S
Asset: RTU-1N VAV'S
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-1N-1 | FLR 1 NORTH RR | METALAIRE | FCI-C2-608 | SERIES | 8 | 420 |  | 100 |  | 420
VAV-1N-1 | FLR 1 NORTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
VRH-1N-1 | FLR 1 LOBBY | METALAIRE |  | HEAT | 8 | 700 |  | 210 |  | 210
Test Date:

## RTU-1N GRD's
National TAB
Project:
RTU-1N GRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-1N-1/C1N1-1 | FLR 1 NORTH RR | D(PL) | 8 | 210 |  |  | 0
CV-1N-1/C1N1-2 | FLR 1 NORTH RR | D(PL) | 8 | 210 |  |  | 0
|  |  |  | 420 |  | 0 | 0
VAV-1N-1/V1N1-1 | FLR 1 NORTH CORE | C | 12X6 | 150 |  |  | 0
VAV-1N-1/V1N1-2 | FLR 1 NORTH CORE | C | 20X10 | 500 |  |  | 0
|  |  |  | 650 |  | 0 | 0
VRH-1N-1/H1N1-1 | FLR 1 LOBBY | B | 8 | 105 |  |  | 0
VRH-1N-1/H1N1-2 | FLR 1 LOBBY | B | 8 | 105 |  |  | 0
VRH-1N-1/H1N1-3 | FLR 1 LOBBY | A | 6 | 70 |  |  | 0
VRH-1N-1/H1N1-4 | FLR 1 LOBBY | D(PL) | 8 | 210 |  |  | 0
VRH-1N-1/H1N1-5 | FLR 1 LOBBY | D(PL) | 8 | 210 |  |  | 0
|  |  |  | 700 |  | 0 | 0
Test Date:

## RTU-1S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-1S Area: FLOOR 1 SOUTH
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040VN8 CNDD8001B0CE 0V00000RT0M8 600 |  | Model Number
Serial Number | C22B01758 |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 20 / 1300 |  | Horsepower / RPM | 7.5 / 800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 20585 |  | Total CFM | 18000
Fan RPM | 1299 |  | Fan RPM | 766
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 15.03 |  | Motor B.H.P. | 5.63
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.618" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-1S VAVs
National TAB
Project: IBP 18 - SHELL
Asset: RTU-1S VAV'S
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-1S-1 | FLR1 SOUTH RR | METALAIRE | FCI-2-606 | SERIES | 6 | 300 |  | 100 |  | 420
FPB-1S-1 | FLR 1 FCS, FARS | METALAIRE | FVI-C2-508 | PARALLEL | 8 | 500 |  | 50
VAV-1S-1 | FLR 1 SOUTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
VAV-1S-2 | FLR 1 SOUTH OFC | METALAIRE |  | COOL | 10 | 1150 |  | 100
Test Date:

## RTU-1S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-1S GRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-1S-1/C1S1-1 | FLR 1 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
CV-1S-1/C1S1-2 | FLR 1 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
FPB-1S-1/F1S1-1 | FLR 1 FCS, FARS | C | 12X6 | 150 |  |  | 0
FPB-1S-1/F1S1-2 | FLR 1 FCS, FARS | C | 14X8 | 350 |  |  | 0
|  |  |  | 500 |  | 0 | 0
VAV-1S-1/V1S1-1 | FLR 1 SOUTH CORE | C | 20X10 | 500 |  |  | 0
VAV-1S-1/V1S1-2 | FLR 1 SOUTH CORE | C | 12X6 | 150 |  |  | 0
|  |  |  | 650 |  | 0 | 0
VAV-1S-2/V1S2-1 | FLR 1 SOUTH OFC | C | 12X6 | 175 |  |  | 0
VAV-1S-2/V1S2-2 | FLR 1 SOUTH OFC | C | 12X6 | 245 |  |  | 0
VAV-1S-2/V1S2-3 | FLR 1 SOUTH OFC | C | 20X10 | 730 |  |  | 0
|  |  |  | 1150 |  | 0 | 0
#DIV/0!
#DIV/0!
#DIV/0!
Test Date:

## RTU-2N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-2N Area: FLOOR 2 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 30 / 1800 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22405 |  | Total CFM | 17000
Fan RPM | 1702 |  | Fan RPM | 482
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 15.03 |  | Motor B.H.P. | 5.63
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.686" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-2N VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-2N VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CVN-2N-1 | FLR 2 NORTH RR | METALAIRE | FCI-C2-608 | SERIES | 8 | 300 |  | 100 |  | 420
FPB-2N-1 | WEST LOBBY EXT | METALAIRE | FVI-C5-514 | PARALLEL | 14 | 2400 |  | 240 |  | 1610
FPB-2N-2 | WEST LOBBY INT | METALAIRE | FVI-C2-510 | PARALLEL | 10 | 1000 |  | 100 |  | 500
VAV-2N-1 | FLR 2 NORTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
Test Date:

## RTU-2N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-2N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-2N-1/C2N1-1 | FLR 2 NORTH RR | D(PL) | 8 | 150 |  |  | 0
CV-2N-1/C2N1-2 | FLR 2 NORTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
FPB-2N-1/F2N1-1 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1/F2N1-2 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1/F2N1-3 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1/F2N1-4 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1/F2N1-5 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1/F2N1-6 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1/F2N1-7 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
FPB-2N-1/F2N1-8 | WEST LOBBY EXT | D(PL) | 12 | 300 |  |  | 0
|  |  |  | 2400 |  | 0 | 0
FPB-2N-2/F2N2-1 | WEST LOBBY INT | D(PL) | 12 | 250 |  |  | 0
FPB-2N-2/F2N2-2 | WEST LOBBY INT | D(PL) | 12 | 250 |  |  | 0
FPB-2N-2/F2N2-3 | WEST LOBBY INT | D(PL) | 12 | 250 |  |  | 0
FPB-2N-2/F2N2-4 | WEST LOBBY INT | D(PL) | 12 | 250 |  |  | 0
|  |  |  | 1000 |  | 0 | 0
VAV-2N-1/V2N1-1 | FLR 2 NORTH CORE | C | 12X6 | 150 |  |  | 0
VAV-2N-1/V2N1-2 | FLR 2 NORTH CORE | C | 20X10 | 500 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## RTU-2S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-2S Area: FLOOR 2 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 30 / 1700 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22115 |  | Total CFM | 17000
Fan RPM | 1685 |  | Fan RPM | 482
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 20.62 |  | Motor B.H.P. | 3.95
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.660" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-2S VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-2S VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-2S-1 | FLR 2 SOUTH RR | METALAIRE | FCI-C2-606 | SERIES | 6 | 300 |  | 100 |  | 300
FPB-2S-1 | EAST LOBBY | METALAIRE | FVI-C5-512 | PARALLEL | 12 | 2000 |  | 200 |  | 1340
FPB-2S-2 | EAST VEST | METALAIRE | FVI-C2-508 | PARALLEL | 8 | 600 |  | 60 |  | 400
VAV-2S-1 | FLR 2 SOUTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
VRH-2S-1 | FLR 2 LOBBY | METALAIRE |  | HEAT | 6 | 300 |  | 100 |  | 100
Test Date:

## RTU-2S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-2S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-2S-1/C2S1-1 | FLR 2 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
CV-2S-1/C2S1-2 | FLR 2 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
FPB-2S-1/F2S1-1 | EAST LOBBY | D(PL) | 12 | 500 |  |  | 0
FPB-2S-1/F2S1-2 | EAST LOBBY | D(PL) | 12 | 500 |  |  | 0
FPB-2S-1/F2S1-3 | EAST LOBBY | D(PL) | 12 | 500 |  |  | 0
FPB-2S-1/F2S1-4 | EAST LOBBY | D(PL) | 12 | 500 |  |  | 0
|  |  |  | 2000 |  | 0 | 0
FPB-2S-2/F2S2-1 | EAST VEST | D(PL) | 12 | 300 |  |  | 0
FPB-2S-2/F2S2-2 | EAST VEST | D(PL) | 12 | 300 |  |  | 0
|  |  |  | 600 |  | 0 | 0
VAV-2S-1/V2S1-1 | FLR 2 SOUTH CORE | C | 20X10 | 500 |  |  | 0
VAV-2S-1/V2S1-2 | FLR 2 SOUTH CORE | C | 12X6 | 150 |  |  | 0
|  |  |  | 650 |  | 0 | 0
VRH-2S-1/H2S1-1 | FLR 2 LOBBY | B | 8 | 500 |  |  | 0
VRH-2S-1/H2S1-2 | FLR 2 LOBBY | B | 8 | 150 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## RTU-3N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-3N Area: FLOOR 3 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 20 / 1400 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21325 |  | Total CFM | 18000
Fan RPM | 1366 |  | Fan RPM | 487
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.48 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.496" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-3N VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-3N VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-3N-1 | FLR 3 NORTH RR | METALAIRE | FCI-C2-608 | SERIES | 8 | 300 |  | 100 |  | 420
VAV-3N-1 | FLR3 NORTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
Test Date:

## RTU-3N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-3N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-3N-1/C3N1-1 | FLR 3 NORTH RR | D(PL) | 8 | 150 |  |  | 0
CV-3N-1/C3N1-2 | FLR 3 NORTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
VAV-3N-1/V3N1-1 | FLR 3 NORTH CORE | C | 12X6 | 150 |  |  | 0
VAV-3N-1/V3N1-2 | FLR 3 NORTH CORE | C | 20X10 | 500 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## RTU-3S
National TAB
Project: IBP 18 - SHELL
System: AHU
Asset: RTU-3S Area: FLOOR 3 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 20 / 1400 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21115 |  | Total CFM | 18000
Fan RPM | 1396 |  | Fan RPM | 487
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 18.56 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.570" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-3S VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-3S VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-3S-1 | FLR 3 SOUTH RR | METALAIRE | FCI-C2-606 | SERIES | 6 | 300 |  | 100 |  | 300
VAV-3S-1 | FLR3 SOUTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
Test Date:

## RTU-3S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-3S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-3S-1/C3S1-1 | FLR 3 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
CV-3S-1/C3S1-2 | FLR 3 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
VAV-3S-1/V3S1-1 | FLR 3 SOUTH CORE | C | 20X10 | 500 |  |  | 0
VAV-3S-1/V3S1-2 | FLR 3 SOUTH CORE | C | 12X6 | 150 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## RTU-4N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-4N Area: FLOOR 4 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 20 / 1400 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 21050 |  | Total CFM | 18000
Fan RPM | 1356 |  | Fan RPM | 487
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.12 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.470" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-4N VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-4N VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-4N-1 | FLR 4 NORTH RR | METALAIRE | FCI-C2-608 | SERIES | 8 | 300 |  | 100 |  | 420
VAV-4N-1 | FLR 4 NORTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
Test Date:

## RTU-4N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-4N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-4N-1/C4N1-1 | FLR 4 NORTH RR | D(PL) | 8 | 150 |  |  | 0
CV-4N-1/C4N1-2 | FLR 4 NORTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
VAV-4N-1/V4N1-1 | FLR 4 NORTH CORE | C | 12X6 | 150 |  |  | 0
VAV-4N-1/V4N1-2 | FLR 4 NORTH CORE | C | 20X10 | 500 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## RTU-4S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-4S Area: FLOOR 4 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7040- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 20 / 1400 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 22180 |  | Total CFM | 18000
Fan RPM | 1398 |  | Fan RPM | 487
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 18.65 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.575" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-4S VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-4S VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-4S-1 | FLR 4 SOUTH RR | METALAIRE | FCI-C2-606 | SERIES | 6 | 300 |  | 100 |  | 300
VAV-4S-1 | FLR 4 SOUTH CORE | METALAIRE |  | COOL | 8 | 650 |  | 100
Test Date:

## RTU-4S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-4S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-4S-1/C4S1-1 | FLR 4 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
CV-4S-1/C4S1-2 | FLR 4 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
VAV-4S-1/V4S1-1 | FLR4 SOUTH CORE | C | 20X10 | 500 |  |  | 0
VAV-4S-1/V4S1-2 | FLR4 SOUTH CORE | C | 12X6 | 150 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## RTU-5N
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-5N Area: FLOOR 5 NORTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7540- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 30 / 1600 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 26860 |  | Total CFM | 18000
Fan RPM | 1554 |  | Fan RPM | 487
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 17.12 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.747" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-5N VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-5N VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-5N-1 | FLR 5 NORTH RR | METALAIRE | FVI-C2-608 | SERIAL | 8 | 300 |  | 100 |  | 420
VRH-5N-1 | FLR 5 NORTH CORE | METALAIRE |  | HEAT | 8 | 650 |  | 100 |  | 200
Test Date:

## RTU-5N GRD's
National TAB
Project: IBP 18 - SHELL
RTU-5N SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-5N-1/C5N1-1 | FLR 5 NORTH RR | D(PL) | 8 | 150 |  |  | 0
CV-5N-1/C5N1-2 | FLR 5 NORTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
VRH-5N-1/H5N1-1 | FLR 5 NORTH CORE | C | 12X6 | 150 |  |  | 0
VRH-5N-1/H5N1-2 | FLR 5 NORTH CORE | C | 20X10 | 500 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## RTU-5S
National TAB
Project: IBP 18 - SHELL
System: RTU
Asset: RTU-5S Area: FLOOR 5 SOUTH
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | SAHLF7540- |  | Model Number
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 35 / 16"x20"x2" |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 30 / 1600 |  | Horsepower / RPM | 5 / 500
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 26605 |  | Total CFM | 18000
Fan RPM | 1543 |  | Fan RPM | 487
Motor HZ |  |  | Motor HZ
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 24.10 |  | Motor B.H.P. | 4.44
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.724" |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
Pre Filters P.D.
Pre Filters P.D.
Total ESP |  |  | Total ESP

## RTU-5S VAV's
National TAB
Project: IBP 18 - SHELL
Asset: RTU-5S VAV's
Asset | Area Served | MFG | Model | Type | Size | Design Max CFM | Max CFM | Design Min CFM | Min CFM | Design Heat CFM | Heat CFM | Ak (max)
CV-5S-1 | FLR 5 SOUTH RR | METALAIRE | FCI-C2-606 | SERIES | 6 | 300 |  | 100 |  | 300
VRH-5S-1 | FLR 5 SOUTH CORE | METALAIRE |  | HEAT | 8 | 650 |  | 100 |  | 200
Test Date:

## RTU-5S GRD's
National TAB
Project: IBP 18 - SHELL
RTU-5S SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
CV-5S-1/C5S1-1 | FLR 5 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
CV-5S-1/C5S1-2 | FLR 5 SOUTH RR | D(PL) | 8 | 150 |  |  | 0
|  |  |  | 300 |  | 0 | 0
VRH-5S-1/H5S1-1 | FLR 5 SOUTH CORE | C | 20X10 | 500 |  |  | 0
VRH-5S-1/H5S1-2 | FLR 5 SOUTH CORE | C | 12X6 | 150 |  |  | 0
|  |  |  | 650 |  | 0 | 0
Test Date:

## FCU-1
National TAB
Project:
Address:
Asset: FCU-1 |  | Area: 110
Unit Data |  |  |  |  | Test Data
MFG | MITSUBISHI ELECTRIC |  |  |  |  | Design | Actual
Model Num | TPEADA0181AA70A |  |  |  | SA CFM | 620
Serial Num | 1YR0079030P904 |  |  |  | Fan Speed
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP
Voltage (rated) | 208
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F1-1 | 110 | A | 10 | 320 |  |  | 0
F1-2 | 110 | A | 10 | 300 |  |  | 0
|  |  |  | 620 |  | 0 | 0

## EF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: EF-1 |  | Area: CORE NORTH RR/JAN
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-20-3-B1-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091822 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | WEG |  |  | Belt Size
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 3050
Voltage (rated) |  | 460 |  |  | Fan RPM | 1004
Amperage (rated) |  | 2.69 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1
[5 empty] | Brake Horse Power | 0.9
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E1-1 | FLR 1 N RR | E | 10 | 280 |  |  | 0
E1-2 | FLR 1 N RR | E | 10 | 280 |  |  | 0
E1-3 | FLR 1 N JAN | H | 12X6 | 50 |  |  | 0
E1-4 | FLR 2 N RR | E | 10 | 280 |  |  | 0
E1-5 | FLR 2 N RR | E | 10 | 280 |  |  | 0
E1-6 | FLR 2 N JAN | H | 12X6 | 50 |  |  | 0
E1-7 | FLR 3 N RR | E | 10 | 280 |  |  | 0
E1-8 | FLR 3 N RR | E | 10 | 280 |  |  | 0
E1-9 | FLR 3 N JAN | H | 12X6 | 50 |  |  | 0
E1-10 | FLR 4 N RR | E | 10 | 280 |  |  | 0
E1-11 | FLR 4 N RR | E | 10 | 280 |  |  | 0
E1-12 | FLR 4 N JAN | H | 12X6 | 50 |  |  | 0
E1-13 | FLR 5 N RR | E | 10 | 280 |  |  | 0
E1-14 | FLR 5 N RR | E | 10 | 280 |  |  | 0
E1-15 | FLR 5 N JAN | H | 12X6 | 50 |  |  | 0
|  |  |  | 3050 |  | 0 | 0
Test Date:
-

## EF-2
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: EF-2 |  | Area: CORE SOUTH RR/JAN
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-20-3-B1-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091824 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | WEG |  |  | Belt Size
Frame |  | 143/5T
Horsepower |  | 1.5 |  |  | Test Data
Motor Rpm |  | 1760 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2350
Voltage (rated) |  | 460 |  |  | Fan RPM | 902
Amperage (rated) |  | 2.07 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1
[5 empty] | Brake Horse Power | 0.6
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E2-1 | FLR 1 S JAN | H | 12X6 | 50 |  |  | 0
E2-2 | FLR 1 S RR | E | 8 | 210 |  |  | 0
E2-3 | FLR 1 S RR | E | 8 | 210 |  |  | 0
E2-4 | FLR 2 S JAN | H | 12X6 | 50 |  |  | 0
E2-5 | FLR 2 S RR | E | 8 | 210 |  |  | 0
E2-6 | FLR 2 S RR | E | 8 | 210 |  |  | 0
E2-7 | FLR 3 S JAN | H | 12X6 | 50 |  |  | 0
E2-8 | FLR 3 S RR | E | 8 | 210 |  |  | 0
E2-9 | FLR 3 S RR | E | 8 | 210 |  |  | 0
E2-10 | FLR 4 S JAN | H | 12X6 | 50 |  |  | 0
E2-11 | FLR 4 S RR | E | 8 | 210 |  |  | 0
E2-12 | FLR 4 S RR | E | 8 | 210 |  |  | 0
E2-13 | FLR 5 S JAN | H | 12X6 | 50 |  |  | 0
E2-14 | FLR 5 S RR | E | 8 | 210 |  |  | 0
E2-15 | FLR 5 S RR | E | 8 | 210 |  |  | 0
|  |  |  | 2350 |  | 0 | 0
Test Date:
-

## SEF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: SEF-1 |  | Area: SMOKE REMOVE NORTH
Unit Data |  |  |  |  | Drive Data
MFG |  |  |  |  | Motor Sheave Size
Model Num |  |  |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 20 |  |  | Test Data
Motor Rpm | [5 empty] | Design | Actual
Phase |  | 3 |  |  | CFM | 2600
Voltage (rated) |  | 460 |  |  | Fan RPM | 659
Amperage (rated) |  |  |  |  | RL Voltage
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.5
[5 empty] | Brake Horse Power | 14.4
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Test Date:
-

## SEF-2
National TAB
Project: IBP 18 - SHELL
System/Unit: EXHAUST FAN
Asset: SEF-2 |  | Area: SMOKE REMOVE SOUTH
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-44-3-B4-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091834 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 20 |  |  | Test Data
Motor Rpm | [5 empty] | Design | Actual
Phase |  | 3 |  |  | CFM | 2600
Voltage (rated) |  | 460 |  |  | Fan RPM | 659
Amperage (rated) |  |  |  |  | RL Voltage
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.5
[5 empty] | Brake Horse Power | 14.4
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Test Date:
-

## EPF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: EPF-1 |  | Area: ELEVATOR HOISTWAY PRESSURIZATION
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-36-5-B4-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091826 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 25 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 22500
Voltage (rated) |  | 460 |  |  | Fan RPM | 1106
Amperage (rated) |  |  |  |  | RL Voltage
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.581
[5 empty] | Brake Horse Power | 17.3
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Test Date:
-

## SPF-1
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: SPF-1 |  | Area: STAIRWELL PRESSURIZATION - STAIR 3
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size | 4
Model Num |  | USF-18-3-B1-00-01-01 |  |  | Motor Bore Size | 0.875
Serial Num |  | 20091838 |  |  | Fan Sheave Size | 5.875
Type |  | CRE UTILITY |  |  | Fan Bore Size | 1.125
[5 empty] | Belt CL Distance | 15.25
Motor Data |  |  |  |  | No of Belts | 2
Motor MFG |  | WEG |  |  | Belt Size | A44
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2800
Voltage (rated) |  | 460 |  |  | Fan RPM | 1168
Amperage (rated) |  | 2.69 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.324
[5 empty] | Brake Horse Power | 0.9
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Test Date:
-

## SPF-2
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: SPF-2 |  | Area: STAIRWELL PRESSURIZATION - STAIR 2
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-18-3-B1-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091849 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | WEG |  |  | Belt Size
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 2800
Voltage (rated) |  | 460 |  |  | Fan RPM | 1168
Amperage (rated) |  | 2.69 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.324
[5 empty] | Brake Horse Power | 0.9
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Test Date:
-

## SPF-3
National TAB
Project: IBP 18 - SHELL
System/Unit: SUPPLY FAN
Asset: SPF-3 |  | Area: STAIRWELL PRESSURIZATION - STAIR 1
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-18-3-B1-00-01-01 |  |  | Motor Bore Size
Serial Num |  | 20091852 |  |  | Fan Sheave Size
Type |  | CRE UTILITY |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  | WEG |  |  | Belt Size
Frame |  | 143/5T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 1740 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 3200
Voltage (rated) |  | 460 |  |  | Fan RPM | 1261
Amperage (rated) |  | 2.69 |  |  | RL Voltage
Service Factor |  | 1.15 |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.423
[5 empty] | Brake Horse Power | 0.9
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Test Date:
-

## SGRD - Blank
National TAB
Project: IBP 18 - SHELL
SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Test Date: