## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3300 | 2800 | 0 | 0 | 3300 | 2800 | 100% | 100%
RTU-2 | KITCHEN | 3300 | 3010 | 0 | 0 | 3300 | 3010 | 100% | 100%
RTU-3 | DINING | 3300 | 3289 | 1400 | 1401 | 1900 | 1888 | 57.58% | 57.4%
RTU-4 | DINING | 3300 | 3320 | 1400 | 1388 | 1900 | 1932 | 57.58% | 58.19%
EF-1 | KITCHEN HD 1 | [10 empty] | 1500 | 1516
EF-2 | KITCHEN HD 2 | [10 empty] | 1700 | 1711
EF-3 | KITCHEN HD 3 | [10 empty] | 2125 | 2119
EF-4 | KITCHEN HD 4 | [10 empty] | 2125 | 2123
EF-5 | KITCHEN HD 5&6 | [10 empty] | 1800 | 1784
EF-6 | RESTROOM | [12 empty] | 500 | 504
TOTALS |  | 13200 | 12419 | 2800 | 2789 | 10400 | 9630 |  |  | 0 | 0 | 9250 | 9253 | 500 | 504
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 10400 | 9630 |  | FRONT |  | -0.1 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 9750 | 9757 |  | SIDE |  | -0.09 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 650 | -127 |  | REAR |  | -0.08 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.09 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390