## RTU-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: RTU-1
Unit Data |  | Test Data
Manufacturer | CARRIER |  | Design | Actual
Model Num | 48FCTN24J2M6-3X5C0 | SF CFM | 8000
Serial Num |  | SF RPM | 1894
Configuration | VERTICAL | RA CFM | 7040
|  | OA CFM | 960
|  | RL VOLTAGE | 460
Num PreFilter | 6 | RL AMPERAGE | 3
PreFilter Size | 20X25X2 | OA Damper Position
|  | Brake Horsepower | 4.96
Motor Data |  | Performance Data
Motor MFG |  |  | Design | Actual
Frame |  | Fan Suction SP
Horsepower |  | Fan Discharge SP
Motor RPM |  | Fan Total SP
Phase | 3 | DX Coil PD * |  | *
Rated Voltage | 460 | Pre Filter PD |  | *combined
Rated Amperage | 3 | Total ESP | 0.75
Service Factor

## RTU-1 GRD's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: RTU-1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-1 | B107 | N | 16X16 | 585 |  |  | 0
1-2 | B114 | E | 9X9 | 50 |  |  | 0
1-3 | B115 | D | 6X6 | 100 |  |  | 0
1-4 | B113 | D | 6X6 | 50 |  |  | 0
1-5 | B112 | B | 8X8 | 130 |  |  | 0
1-6 | B109 | F | 12X12 | 360 |  |  | 0
1-7 | B107 | N | 16X16 | 585 |  |  | 0
1-8 | B107 | N | 16X16 | 585 |  |  | 0
1-9 | B107 | N | 16X16 | 585 |  |  | 0
1-10 | B107 | N | 16X16 | 585 |  |  | 0
1-11 | B107 | N | 16X16 | 585 |  |  | 0
1-12 | B108 | F | 12X12 | 400 |  |  | 0
1-13 | B108 | F | 12X12 | 400 |  |  | 0
1-14 | B106 | G | 15X15 | 600 |  |  | 0
1-15 | B106 | G | 15X15 | 600 |  |  | 0
1-16 | B106 | G | 15X15 | 600 |  |  | 0
1-17 | B106 | G | 15X15 | 600 |  |  | 0
1-18 | B106 | G | 15X15 | 600 |  |  | 0
|  |  |  | 8000 |  | 0 | 0
Asset: RTU-1 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R1-1 | B109 | M | 12X12 | 315 |  |  | 0
R1-2 | B107 | P | 22X20 | 1345 |  |  | 0
R1-3 | B107 | P | 22X20 | 1345 |  |  | 0
R1-4 | B107 | P | 22X20 | 1345 |  |  | 0
R1-5 | B107 | P | 22X20 | 1345 |  |  | 0
R1-6 | B107 | P | 22X20 | 1345 |  |  | 0
|  |  |  | 7040 |  | 0 | 0

## AHU-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-1 |  | Area: CLASSROOMS
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 20X25X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 256T |  | Motor MFG / Frame | / 213T
Horsepower / RPM | 10.0 / 1200 |  | Horsepower / RPM | 3.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 480 / 3
Rated Amperage / SF | 14.1 |  | Rated Amperage / SF | 4.6 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM [1] | 9800 |  | Total CFM | 9800
Min OA CFM | 1720
Fan RPM | 1474 |  | Fan RPM | 1336
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 14.1 |  | RL Amperage | 4.6
Motor B.H.P. | 9.5 |  | Motor B.H.P. | 2.7
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.04 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.25 |  | Total ESP
NOTES: | [1] AHU SUPPLY IS 9800 CFM, VAV MAX TOTAL IS 11850 CFM

## AHU-1 VAV's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-1 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-1.01 | A159 | HEAT | SINGLE | 5 | 250 |  | 70 |  | 130
VAV-1.02 | A163 | HEAT | SINGLE | 12 | 1455 |  | 370 |  | 730
VAV-1.03 | A156 | HEAT | SINGLE | 12 | 1515 |  | 380 |  | 760
VAV-1.04 | A165 | HEAT | SINGLE | 10 | 1030 |  | 260 |  | 520
VAV-1.05 | A154 | HEAT | SINGLE | 10 | 1210 |  | 310 |  | 610
VAV-1.06 | A167 | HEAT | SINGLE | 10 | 1030 |  | 260 |  | 520
VAV-1.07 | A152 | HEAT | SINGLE | 12 | 1490 |  | 380 |  | 750
VAV-1.08 | A169 | HEAT | SINGLE | 10 | 1030 |  | 260 |  | 520
VAV-1.09 | A173 | HEAT | SINGLE | 10 | 1160 |  | 290 |  | 580
VAV-1.10 | A172 | COOL | SINGLE | 10 | 500 |  | 150 |  | 0
VAV-1.11 | A150 | HEAT | SINGLE | 10 | 1180 |  | 300 |  | 590
11850
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-1 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V102-1 | A164 | C | 6X6 | 50 |  |  | 0
V102-2 | A199A | F | 12X12 | 425 |  |  | 0
V102-3 | A163 | E | 9X9 | 245 |  |  | 0
V102-4 | A163 | E | 9X9 | 245 |  |  | 0
V102-5 | A163 | E | 9X9 | 245 |  |  | 0
V102-6 | A163 | E | 9X9 | 245 |  |  | 0
VAV-1.02 |  |  |  | 1455 |  | 0 | 0
V103-1 | A199 | F | 12X12 | 310 |  |  | 0
V103-2 | A158 | B | 8X8 | 75 |  |  | 0
V103-3 | A157 | C | 6X6 | 50 |  |  | 0
V103-4 | A156 | E | 9X9 | 270 |  |  | 0
V103-5 | A156 | E | 9X9 | 270 |  |  | 0
V103-6 | A156 | E | 9X9 | 270 |  |  | 0
V103-7 | A156 | E | 9X9 | 270 |  |  | 0
VAV-1.03 |  |  |  | 1515 |  | 0 | 0
V104-1 | A166 | C | 6X6 | 50 |  |  | 0
V104-2 | A165 | E | 9X9 | 245 |  |  | 0
V104-3 | A165 | E | 9X9 | 245 |  |  | 0
V104-4 | A165 | E | 9X9 | 245 |  |  | 0
V104-5 | A165 | E | 9X9 | 245 |  |  | 0
VAV-1.04 |  |  |  | 1030 |  | 0 | 0
V105-1 | A160 | D | 6X6 | 80 |  |  | 0
V105-2 | A155 | C | 6X6 | 50 |  |  | 0
V105-3 | A154 | E | 9X9 | 270 |  |  | 0
V105-4 | A154 | E | 9X9 | 270 |  |  | 0
V105-5 | A154 | E | 9X9 | 270 |  |  | 0
V105-6 | A154 | E | 9X9 | 270 |  |  | 0
VAV-1.05 |  |  |  | 1210 |  | 0 | 0

## AHU-1 SGRD's (2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V106-1 | A168 | C | 6X6 | 50 |  |  | 0
V106-2 | A167 | E | 9X9 | 245 |  |  | 0
V106-3 | A167 | E | 9X9 | 245 |  |  | 0
V106-4 | A167 | E | 9X9 | 245 |  |  | 0
V106-5 | A167 | E | 9X9 | 245 |  |  | 0
VAV-1.06 |  |  |  | 1030 |  | 0 | 0
V107-1 | A162 | C | 6X6 | 50 |  |  | 0
V107-2 | A199 | F | 12X12 | 310 |  |  | 0
V107-3 | A152 | E | 9X9 | 270 |  |  | 0
V107-4 | A152 | E | 9X9 | 270 |  |  | 0
V107-5 | A153 | C | 6X6 | 50 |  |  | 0
V107-6 | A152 | E | 9X9 | 270 |  |  | 0
V107-7 | A152 | E | 9X9 | 270 |  |  | 0
VAV-1.07 |  |  |  | 1490 |  | 0 | 0
V108-1 | A170 | C | 6X6 | 50 |  |  | 0
V108-2 | A169 | E | 9X9 | 245 |  |  | 0
V108-3 | A169 | E | 9X9 | 245 |  |  | 0
V108-4 | A169 | E | 9X9 | 245 |  |  | 0
V108-5 | A169 | E | 9X9 | 245 |  |  | 0
VAV-1.08 |  |  |  | 1030 |  | 0 | 0
V109-1 | A173 | F | 12X12 | 350 |  |  | 0
V109-2 | A174 | F | 12X12 | 310 |  |  | 0
V109-3 | A171 | E | 9X9 | 250 |  |  | 0
V109-4 | A171 | E | 9X9 | 250 |  |  | 0
VAV-1.09 |  |  |  | 1160 |  | 0 | 0
V110-1 | A172 | F | 18X10 | 500 |  |  | 0
VAV-1.10 |  |  |  | 500 |  | 0 | 0

## AHU-1 SGRD's (3)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V111-1 | A161 | C | 6X6 | 50 |  |  | 0
V111-2 | A150 | E | 9X9 | 270 |  |  | 0
V111-3 | A150 | E | 9X9 | 270 |  |  | 0
V111-4 | A151 | C | 6X6 | 50 |  |  | 0
V111-5 | A150 | E | 9X9 | 270 |  |  | 0
V111-6 | A150 | E | 9X9 | 270 |  |  | 0
VAV-1.11 |  |  |  | 1180 |  | 0 | 0

## AHU-2
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-2 |  | Area: CLASSROOMS
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 20X25X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 256T |  | Motor MFG / Frame | / 213T
Horsepower / RPM | 10.0 / 1200 |  | Horsepower / RPM | 3.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 480 / 3
Rated Amperage / SF | 14.1 |  | Rated Amperage / SF | 4.6 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM [1] | 9100 |  | Total CFM | 9100
Min OA CFM | 1590
Fan RPM | 1664 |  | Fan RPM | 1248
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 14.1 |  | RL Amperage | 4.6
Motor B.H.P. | 8.2 |  | Motor B.H.P. | 2.3
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.69 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.25 |  | Total ESP
NOTES: | [1] AHU SUPPLY IS 9100 CFM, VAV MAX TOTAL IS 11310 CFM

## AHU-2 VAV's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-2 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-2.01 | A148 | HEAT | SINGLE | 5 | 250 |  | 70 |  | 130
VAV-2.02 | A175 | HEAT | SINGLE | 10 | 1010 |  | 260 |  | 510
VAV-2.03 | A146 | HEAT | SINGLE | 10 | 1130 |  | 290 |  | 570
VAV-2.04 | A149 | COOL | SINGLE | 10 | 500 |  | 150 |  | 0
VAV-2.05 | A177 | HEAT | SINGLE | 10 | 1100 |  | 280 |  | 550
VAV-2.06 | A144 | HEAT | SINGLE | 12 | 1440 |  | 360 |  | 720
VAV-2.07 | A179 | HEAT | SINGLE | 10 | 1060 |  | 270 |  | 530
VAV-2.08 | A142 | HEAT | SINGLE | 12 | 1440 |  | 360 |  | 720
VAV-2.09 | A181 | HEAT | SINGLE | 10 | 900 |  | 230 |  | 450
VAV-2.10 | A140 | HEAT | SINGLE | 10 | 1060 |  | 270 |  | 530
VAV-2.11 | A184 | HEAT | SINGLE | 12 | 1420 |  | 360 |  | 710
11310
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-2 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V202-1 | A175 | E | 9X9 | 240 |  |  | 0
V202-2 | A176 | C | 6X6 | 50 |  |  | 0
V202-3 | A175 | E | 9X9 | 240 |  |  | 0
V202-4 | A175 | E | 9X9 | 240 |  |  | 0
V202-5 | A175 | E | 9X9 | 240 |  |  | 0
VAV-2.02 |  |  |  | 1010 |  | 0 | 0
V203-1 | A146 | E | 9X9 | 270 |  |  | 0
V203-2 | A146 | E | 9X9 | 270 |  |  | 0
V203-3 | A147 | C | 6X6 | 50 |  |  | 0
V203-4 | A146 | E | 9X9 | 270 |  |  | 0
V203-5 | A146 | E | 9X9 | 270 |  |  | 0
VAV-2.03 |  |  |  | 1130 |  | 0 | 0
V204-1 | A149 | F | 18X10 | 500 |  |  | 0
VAV-2.04 |  |  |  | 500 |  | 0 | 0
V205-1 | A183 | E | 9X9 | 90 |  |  | 0
V205-2 | A177 | E | 9X9 | 240 |  |  | 0
V205-3 | A178 | C | 6X6 | 50 |  |  | 0
V205-4 | A177 | E | 9X9 | 240 |  |  | 0
V205-5 | A177 | E | 9X9 | 240 |  |  | 0
V205-6 | A177 | E | 9X9 | 240 |  |  | 0
VAV-2.05 |  |  |  | 1100 |  | 0 | 0
V206-1 | A198 | F | 12X12 | 310 |  |  | 0
V206-2 | A144 | E | 9X9 | 270 |  |  | 0
V206-3 | A144 | E | 9X9 | 270 |  |  | 0
V206-4 | A145 | C | 6X6 | 50 |  |  | 0
V206-5 | A144 | E | 9X9 | 270 |  |  | 0
V206-6 | A144 | E | 9X9 | 270 |  |  | 0
VAV-2.06 |  |  |  | 1440 |  | 0 | 0

## AHU-2 SGRD's (2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V2.07-1 | A182 | C | 6X6 | 50 |  |  | 0
V2.07-2 | A179 | E | 9X9 | 240 |  |  | 0
V2.07-3 | A180 | C | 6X6 | 50 |  |  | 0
V2.07-4 | A179 | E | 9X9 | 240 |  |  | 0
V2.07-5 | A179 | E | 9X9 | 240 |  |  | 0
V2.07-6 | A179 | E | 9X9 | 240 |  |  | 0
VAV-2.07 |  |  |  | 1060 |  | 0 | 0
V208-1 | A174 | E | 9X9 | 310 |  |  | 0
V208-2 | A142 | E | 9X9 | 270 |  |  | 0
V208-3 | A142 | E | 9X9 | 270 |  |  | 0
V208-4 | A143 | C | 6X6 | 50 |  |  | 0
V208-5 | A142 | E | 9X9 | 270 |  |  | 0
V208-6 | A142 | E | 9X9 | 270 |  |  | 0
VAV-2.08 |  |  |  | 1440 |  | 0 | 0
V209-1 | A181 | E | 9X9 | 225 |  |  | 0
V209-2 | A181 | E | 9X9 | 225 |  |  | 0
V209-3 | A181 | E | 9X9 | 225 |  |  | 0
V209-4 | A181 | E | 9X9 | 225 |  |  | 0
VAV-2.09 |  |  |  | 900 |  | 0 | 0
V210-1 | A141 | E | 9X9 | 100 |  |  | 0
V210-2 | A140 | E | 9X9 | 240 |  |  | 0
V210-3 | A140 | E | 9X9 | 240 |  |  | 0
V210-4 | A140 | E | 9X9 | 240 |  |  | 0
V210-5 | A140 | E | 9X9 | 240 |  |  | 0
VAV-2.10 |  |  |  | 1060 |  | 0 | 0

## AHU-2 SGRD's (3)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V211-1 | A184 | C | 6X6 | 50 |  |  | 0
V211-2 | A186 | E | 99 | 275 |  |  | 0
V211-3 | A185 | E | 9X9 | 275 |  |  | 0
V211-4 | A102 | B | 18X10 | 410 |  |  | 0
V211-5 | A102 | E | 9X9 | 410 |  |  | 0
VAV-2.11 |  |  |  | 1420 |  | 0 | 0

## AHU-3
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-3 |  | Area: ADMIN
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39M
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 16X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 213T |  | Motor MFG / Frame | / 182T
Horsepower / RPM | 7.5 / 1800 |  | Horsepower / RPM | 3 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 9.5 / |  | Rated Amperage / SF | 4.1
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM [1] | 6200 |  | Total CFM | 6200
Min OA CFM | 1500
Fan RPM | 2064 |  | Fan RPM | 2043
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 9.5 |  | RL Amperage | 4.1
Motor B.H.P. | 5.8 |  | Motor B.H.P. | 2.1
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.93 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.25 |  | Total ESP
NOTES: | [1] AHU SUPPLY IS 6200 CFM, VAV MAX TOTAL IS 7985 CFM

## AHU-3 VAV's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-3 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-3.01 | A124 | HEAT | SINGLE | 5 | 155 |  | 40 |  | 80
VAV-3.02 | A119 | COOL | SINGLE | 10 | 500 |  | 150 |  | 0
VAV-3.03 | A115 | HEAT | SINGLE | 10 | 600 |  | 150 |  | 300
VAV-3.04 | A118 | COOL | SINGLE | 10 | 500 |  | 150 |  | 0
VAV-3.05 | A114 | HEAT | SINGLE | 8 | 395 |  | 100 |  | 200
VAV-3.06 | A116 | HEAT | SINGLE | 5 | 175 |  | 50 |  | 90
VAV-3.07 | A113 | HEAT | SINGLE | 6 | 310 |  | 80 |  | 160
VAV-3.08 | A112 | HEAT | SINGLE | 8 | 375 |  | 100 |  | 190
VAV-3.09 | A121 | HEAT | SINGLE | 10 | 595 |  | 150 |  | 300
VAV-3.10 | A111 | HEAT | SINGLE | 8 | 625 |  | 160 |  | 320
VAV-3.11 | A106 | HEAT | SINGLE | 5 | 225 |  | 60 |  | 120
VAV-3.12 | A108 | HEAT | SINGLE | 10 | 710 |  | 180 |  | 360
VAV-3.13 | A105 | HEAT | SINGLE | 10 | 760 |  | 190 |  | 380
VAV-3.14 | A127 | HEAT | SINGLE | 6 | 320 |  | 80 |  | 160
VAV-3.15 | A125 | HEAT | SINGLE | 6 | 260 |  | 70 |  | 130
VAV-3.16 | A126 | HEAT | SINGLE | 8 | 400 |  | 100 |  | 200
VAV-3.17 | A101 | HEAT | SINGLE | 8 | 620 |  | 160 |  | 310
VAV-3.18 | A104 | HEAT | SINGLE | 8 | 460 |  | 120 |  | 230
7985
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-3 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V301-1 | A124 | E | 9X9 | 155 |  |  | 0
VAV-3.01 |  |  |  | 155 |  | 0 | 0
V302-1 | A119 | B | 1810 | 500 |  |  | 0
VAV-3.02 |  |  |  | 500 |  | 0 | 0
V303-1 | A129 | E | 9X9 | 300 |  |  | 0
V303-2 | A115 | E | 9X9 | 300 |  |  | 0
VAV-3.03 |  |  |  | 600 |  | 0 | 0
V305-1 | A114 | E | 9X9 | 180 |  |  | 0
V305-2 | A114 | E | 9X9 | 180 |  |  | 0
V305-3 | A117 | B | 6X6 | 35 |  |  | 0
VAV-3.05 |  |  |  | 395 |  | 0 | 0
V306-1 | A120 | E | 9X9 | 50 |  |  | 0
V306-2 | A116 | E | 9X9 | 125 |  |  | 0
VAV-3.06 |  |  |  | 175 |  | 0 | 0
V307-1 | A113 | F | 12X12 | 310 |  |  | 0
VAV-3.07 |  |  |  | 310 |  | 0 | 0
V308-1 | A112 | F | 12X12 | 375 |  |  | 0
VAV-3.08 |  |  |  | 375 |  | 0 | 0
V309-1 | A121 | E | 9X9 | 200 |  |  | 0
V309-2 | A123 | C | 6X6 | 50 |  |  | 0
V309-3 | A122 | C | 6X6 | 50 |  |  | 0
V309-4 | A121 | E | 9X9 | 145 |  |  | 0
V309-5 | A121 HALL | E | 9X9 | 150 |  |  | 0
VAV-3.09 |  |  |  | 595 |  | 0 | 0

## AHU-3 SGRD's (2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V310-1 | A111 | E | 9X9 | 150 |  |  | 0
V310-2 | A110 | E | 9X9 | 150 |  |  | 0
V310-3 | A129 | E | 9X9 | 175 |  |  | 0
V310-4 | A109 | E | 9X9 | 150 |  |  | 0
VAV-3.10 |  |  |  | 625 |  | 0 | 0
V311-1 | A107 | C | 6X6 | 50 |  |  | 0
V311-2 | A106 | E | 9X9 | 175 |  |  | 0
VAV-3.11 |  |  |  | 225 |  | 0 | 0
V312-1 | A108 | F | 12X12 | 355 |  |  | 0
V312-2 | A108 | F | 12X12 | 355 |  |  | 0
VAV-3.12 |  |  |  | 710 |  | 0 | 0
V313-1 | A105 | E | 9X9 | 180 |  |  | 0
V313-2 | A105 | E | 9X9 | 180 |  |  | 0
V313-3 | A100A | E | 9X9 | 120 |  |  | 0
V313-4 | A100B | E | 9X9 | 140 |  |  | 0
V313-5 | A100C | E | 9X9 | 140 |  |  | 0
VAV-3.13 |  |  |  | 760 |  | 0 | 0
V314-1 | A127 | F | 12X12 | 320 |  |  | 0
VAV-3.14 |  |  |  | 320 |  | 0 | 0
V315-1 | A125 | E | 9X9 | 130 |  |  | 0
V315-2 | A128 | E | 9X9 | 130 |  |  | 0
VAV-3.15 |  |  |  | 260 |  | 0 | 0
V316-1 | A121 HALL | E | 9X9 | 150 |  |  | 0
V316-2 | A126 | D | 6X6 | 125 |  |  | 0
V316-3 | A126 | D | 6X6 | 125 |  |  | 0
VAV-3.16 |  |  |  | 400 |  | 0 | 0

## AHU-3 SGRD's (3)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-3 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V317-1 | A101 | E | 9X9 | 220 |  |  | 0
V317-2 | A101 | F | 12X12 | 400 |  |  | 0
VAV-3.17 |  |  |  | 620 |  | 0 | 0
V318-1 | A104 | F | 12X12 | 385 |  |  | 0
V318-2 | A103 | D | 6X6 | 75 |  |  | 0
VAV-3.17 |  |  |  | 460 |  | 0 | 0

## AHU-4
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-4 |  | Area: MEDIA
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 16X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 213T |  | Motor MFG / Frame | / 145T
Horsepower / RPM | 7.5 / 1800 |  | Horsepower / RPM | 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 9.5 / |  | Rated Amperage / SF | 2.9 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM [1] | 6000 |  | Total CFM | 6000
Min OA CFM | 1400
Fan RPM | 2023 |  | Fan RPM | 1981
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 9.5 |  | RL Amperage | 2.9
Motor B.H.P. | 5.5 |  | Motor B.H.P. | 1.9
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.84 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.25 |  | Total ESP
NOTES: | [1] AHU SUPPLY IS 6000 CFM, VAV MAX TOTAL IS 6840 CFM

## AHU-4 VAV's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-4 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-4.01 | A135 | HEAT | SINGLE | 8 | 390 |  | 100 |  | 200
VAV-4.02 | A134 | HEAT | SINGLE | 6 | 310 |  | 80 |  | 160
VAV-4.03 | A130 | HEAT | SINGLE | 10 | 1200 |  | 300 |  | 600
VAV-4.04 | A130 | HEAT | SINGLE | 12 | 1610 |  | 410 |  | 810
VAV-4.05 | A133 | HEAT | SINGLE | 6 | 350 |  | 90 |  | 180
VAV-4.06 | A130 | HEAT | SINGLE | 10 | 690 |  | 180 |  | 350
VAV-4.07 | A196 | HEAT | SINGLE | 10 | 900 |  | 230 |  | 450
VAV-4.08 | A131 | HEAT | SINGLE | 10 | 890 |  | 230 |  | 450
VAV-4.09 | A280 | HEAT | SINGLE | 8 | 500 |  | 130 |  | 250
6840
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-4 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-4 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V401-1 | A135 | E | 9X9 | 390 |  |  | 0
VAV-4.01 |  |  |  | 390 |  | 0 | 0
V402-1 | A134 | E | 9X9 | 155 |  |  | 0
V402-2 | A134 | E | 9X9 | 155 |  |  | 0
VAV-4.02 |  |  |  | 310 |  | 0 | 0
V403-1 | A130 | F | 12X12 | 400 |  |  | 0
V403-2 | A130 | F | 12X12 | 400 |  |  | 0
V403-3 | A130 | F | 12X12 | 400 |  |  | 0
VAV-4.03 |  |  |  | 1200 |  | 0 | 0
V404-1 | A130 | E | 9x9 | 230 |  |  | 0
V404-2 | A130 | E | 9x9 | 230 |  |  | 0
V404-3 | A130 | E | 9x9 | 230 |  |  | 0
V404-4 | A130 | E | 9x9 | 230 |  |  | 0
V404-5 | A130 | E | 9x9 | 230 |  |  | 0
V404-6 | A130 | E | 9x9 | 230 |  |  | 0
V404-7 | A130 | E | 9x9 | 230 |  |  | 0
VAV-4.04 |  |  |  | 1610 |  | 0 | 0
V405-1 | A132 | E | 9X9 | 140 |  |  | 0
V405-2 | A133 | D | 6X6 | 110 |  |  | 0
V405-3 | A136 | D | 6X6 | 100 |  |  | 0
VAV-4.05 |  |  |  | 350 |  | 0 | 0
V406-1 | A130 | E | 9x9 | 230 |  |  | 0
V406-2 | A130 | E | 9x9 | 230 |  |  | 0
V406-3 | A130 | E | 9x9 | 230 |  |  | 0
VAV-4.06 |  |  |  | 690 |  | 0 | 0

## AHU-4 SGRD's (2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-4 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V407-1 | A196 | B | 10X8 | 300 |  |  | 0
V407-2 | A196 | E | 9X9 | 200 |  |  | 0
V407-3 | A197 | F | 12X12 | 400 |  |  | 0
VAV-4.07 |  |  |  | 900 |  | 0 | 0
V408-1 | A131A | D | 6X6 | 50 |  |  | 0
V408-2 | A131 | E | 9X9 | 210 |  |  | 0
V408-3 | A131 | E | 9X9 | 210 |  |  | 0
V408-4 | A131 | E | 9X9 | 210 |  |  | 0
V408-5 | A131 | E | 9X9 | 210 |  |  | 0
VAV-4.08 |  |  |  | 890 |  | 0 | 0

## AHU-5
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-5 |  | Area: MULTIPURPOSE
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 10 / 20X24X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 215T |  | Motor MFG / Frame | / 215T
Horsepower / RPM | 5.0 / 1200 |  | Horsepower / RPM | 5.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 7.3 |  | Rated Amperage / SF | 7.3 /
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 12500 |  | Total CFM | 12500
Min OA CFM | 4700
Fan RPM | 1590 |  | Fan RPM | 1239
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 7.3 |  | RL Amperage | 7.3
Motor B.H.P. | 8.1 |  | Motor B.H.P. | 3.8
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 2.70 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.00 |  | Total ESP

## AHU-5 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-5 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
5-1 | B100 | FABRIC | 28 | 5000 |  |  | 0
5-2 | B100 | E | 9X9 | 225 |  |  | 0
5-3 | B100 | B | 8X8 | 225 |  |  | 0
5-4 | B100 | A | 18X5 | 400 |  |  | 0
5-5 | B100 | A | 18X5 | 400 |  |  | 0
5-6 | B100 | FABRIC | 28 | 5000 |  |  | 0
5-7 | B100 | F | 12X12 | 450 |  |  | 0
5-8 | B100 | A | 18X5 | 400 |  |  | 0
5-9 | B100 | A | 18X5 | 400 |  |  | 0
|  |  |  | 12500 |  | 0 | 0

## AHU-6
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-6 |  | Area: DINING
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 20X25X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 256T |  | Motor MFG / Frame | / 215T
Horsepower / RPM | 10 / 1200 |  | Horsepower / RPM | 5.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 14.1 |  | Rated Amperage / SF | 7.3
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 10600 |  | Total CFM | 10600
Min OA CFM | 3000
Fan RPM | 1429 |  | Fan RPM | 1437
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 14.1 |  | RL Amperage | 7.3
Motor B.H.P. | 8.3 |  | Motor B.H.P. | 3.3
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.21 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 1.00 |  | Total ESP

## AHU-6 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-6 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
6-1 | B101 | G | 15X15 | 610 |  |  | 0
6-2 | B101 | G | 15X15 | 585 |  |  | 0
6-3 | B101 | G | 15X15 | 585 |  |  | 0
6-4 | B101 | G | 15X15 | 585 |  |  | 0
6-5 | B101 | G | 15X15 | 585 |  |  | 0
6-6 | B101 | G | 15X15 | 605 |  |  | 0
6-7 | B101 | G | 15X15 | 585 |  |  | 0
6-8 | B101 | G | 15X15 | 585 |  |  | 0
6-9 | B101 | G | 15X15 | 610 |  |  | 0
6-10 | B101 | G | 15X15 | 585 |  |  | 0
6-11 | B101 | G | 15X15 | 585 |  |  | 0
6-12 | B101 | G | 15X15 | 585 |  |  | 0
6-13 | B101 | G | 15X15 | 585 |  |  | 0
6-14 | B101 | G | 15X15 | 585 |  |  | 0
6-15 | B101 | G | 15X15 | 585 |  |  | 0
6-16 | B101 | G | 15X15 | 585 |  |  | 0
6-17 | B101 | G | 15X15 | 585 |  |  | 0
6-18 | B101 | G | 15X15 | 585 |  |  | 0
|  |  |  | 10600 |  | 0 | 0

## AHU-7
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-7 |  | Area: CLASSROOMS
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 10 / 20X24X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 215T |  | Motor MFG / Frame | / 213T
Horsepower / RPM | 10.0 / 1800 |  | Horsepower / RPM | 3.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 12.0 |  | Rated Amperage / SF | 4.6
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 15100 |  | Total CFM | 15100
Min OA CFM | 2300
Fan RPM | 1956 |  | Fan RPM | 1480
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 12.0 |  | RL Amperage | 4.6
Motor B.H.P. | 15.3 |  | Motor B.H.P. | 5.0
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.21 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.25 |  | Total ESP

## AHU-7 VAV's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-7 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-7.01 | A231 | HEAT | SINGLE | 5 | 250 |  | 70 |  | 130
VAV-7.02 | A232 | HEAT | SINGLE | 12 | 1445 |  | 370 |  | 730
VAV-7.03 | A229 | HEAT | SINGLE | 12 | 1435 |  | 360 |  | 720
VAV-7.04 | A233 | HEAT | SINGLE | 10 | 960 |  | 240 |  | 480
VAV-7.05 | A228 | HEAT | SINGLE | 10 | 1200 |  | 300 |  | 466
VAV-7.06 | A234 | HEAT | SINGLE | 10 | 960 |  | 240 |  | 480
VAV-7.07 | A227 | HEAT | SINGLE | 12 | 1360 |  | 340 |  | 680
VAV-7.08 | A237 | HEAT | SINGLE | 10 | 1080 |  | 270 |  | 540
VAV-7.09 | A224 | HEAT | SINGLE | 10 | 1195 |  | 300 |  | 600
VAV-7.10 | A238 | HEAT | SINGLE | 10 | 960 |  | 240 |  | 480
VAV-7.11 | A223 | HEAT | SINGLE | 12 | 1360 |  | 340 |  | 680
VAV-7.12 | A239 | HEAT | SINGLE | 10 | 960 |  | 240 |  | 480
VAV-7.13 | A244 | COOL | SINGLE | 10 | 500 |  | 150 |  | 0
VAV-7.14 | A222 | HEAT | SINGLE | 10 | 1200 |  | 300 |  | 600
VAV-7.15 | A242 | HEAT | SINGLE | 10 | 720 |  | 180 |  | 360
VAV-7.16 | A240 | HEAT | SINGLE | 6 | 325 |  | 90 |  | 170
VAV-7.17 | A221 | HEAT | SINGLE | 10 | 1080 |  | 270 |  | 540
16990
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-7 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-7 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V702-1 | A235 | TF | 8 | 120 |  |  | 0
V702-2 | A232 | E | 9X9 | 240 |  |  | 0
V702-3 | A232 | E | 9X9 | 240 |  |  | 0
V702-4 | A261 | F | 12X12 | 365 |  |  | 0
V702-5 | A232 | E | 9X9 | 240 |  |  | 0
V702-6 | A232 | E | 9X9 | 240 |  |  | 0
VAV-7.02 |  |  |  | 1445 |  | 0 | 0
V703-1 | A259 | E | 9X9 | 280 |  |  | 0
V703-2 | A230 | B | 6X6 | 75 |  |  | 0
V703-3 | A229 | E | 9X9 | 270 |  |  | 0
V703-4 | A229 | E | 9X9 | 270 |  |  | 0
V703-5 | A229 | E | 9X9 | 270 |  |  | 0
V703-6 | A229 | E | 9X9 | 270 |  |  | 0
VAV-7.03 |  |  |  | 1435 |  | 0 | 0
V704-1 | A233 | E | 9X9 | 240 |  |  | 0
V704-2 | A233 | E | 9X9 | 240 |  |  | 0
V704-3 | A233 | E | 9X9 | 240 |  |  | 0
V704-4 | A233 | E | 9X9 | 240 |  |  | 0
VAV-7.04 |  |  |  | 960 |  | 0 | 0
V705-1 | A226 | TF | 8 | 120 |  |  | 0
V705-2 | A228 | E | 9X9 | 270 |  |  | 0
V705-3 | A228 | E | 9X9 | 270 |  |  | 0
V705-4 | A228 | E | 9X9 | 270 |  |  | 0
V705-5 | A228 | E | 9X9 | 270 |  |  | 0
VAV-7.05 |  |  |  | 1200 |  | 0 | 0

## AHU-7 SGRD's (2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-7 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V706-1 | A234 | E | 9X9 | 240 |  |  | 0
V706-2 | A234 | E | 9X9 | 240 |  |  | 0
V706-3 | A234 | E | 9X9 | 240 |  |  | 0
V706-4 | A234 | E | 9X9 | 240 |  |  | 0
VAV-7.06 |  |  |  | 960 |  | 0 | 0
V707-1 | A259 | E | 9X9 | 280 |  |  | 0
V707-2 | A227 | E | 9X9 | 270 |  |  | 0
V707-3 | A227 | E | 9X9 | 270 |  |  | 0
V707-4 | A227 | E | 9X9 | 270 |  |  | 0
V707-5 | A227 | E | 9X9 | 270 |  |  | 0
VAV-7.07 |  |  |  | 1360 |  | 0 | 0
V708-1 | A236 | TF | 8 | 120 |  |  | 0
V708-2 | A237 | E | 9X9 | 240 |  |  | 0
V708-3 | A237 | E | 9X9 | 240 |  |  | 0
V708-4 | A237 | E | 9X9 | 240 |  |  | 0
V708-5 | A237 | E | 9X9 | 240 |  |  | 0
VAV-7.08 |  |  |  | 1080 |  | 0 | 0
V709-1 | A225 | TF | 8 | 115 |  |  | 0
V709-2 | A224 | E | 9X9 | 270 |  |  | 0
V709-3 | A224 | E | 9X9 | 270 |  |  | 0
V709-4 | A224 | E | 9X9 | 270 |  |  | 0
V709-5 | A224 | E | 9X9 | 270 |  |  | 0
VAV-7.09 |  |  |  | 1195 |  | 0 | 0
V710-1 | A238 | E | 9X9 | 240 |  |  | 0
V710-2 | A238 | E | 9X9 | 240 |  |  | 0
V710-3 | A238 | E | 9X9 | 240 |  |  | 0
V710-4 | A238 | E | 9X9 | 240 |  |  | 0
VAV-7.10 |  |  |  | 960 |  | 0 | 0

## AHU-7 SGRD's (3)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-7 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V711-1 | A259 | E | 9X9 | 280 |  |  | 0
V711-2 | A223 | E | 9X9 | 270 |  |  | 0
V711-3 | A223 | E | 9X9 | 270 |  |  | 0
V711-4 | A223 | E | 9X9 | 270 |  |  | 0
V711-5 | A223 | E | 9X9 | 270 |  |  | 0
VAV-7.11 |  |  |  | 1360 |  | 0 | 0
V712-1 | A239 | E | 9X9 | 240 |  |  | 0
V712-2 | A239 | E | 9X9 | 240 |  |  | 0
V712-3 | A239 | E | 9X9 | 240 |  |  | 0
V712-4 | A239 | E | 9X9 | 240 |  |  | 0
VAV-7.12 |  |  |  | 960 |  | 0 | 0
V713-1 | A244 | B | 18X10 | 500 |  |  | 0
VAV-7.13 |  |  |  | 500 |  | 0 | 0
V714-1 | A221A | TF | 8 | 120 |  |  | 0
V714-2 | A222 | E | 9X9 | 270 |  |  | 0
V714-3 | A222 | E | 9X9 | 270 |  |  | 0
V714-4 | A222 | E | 9X9 | 270 |  |  | 0
V714-5 | A222 | E | 9X9 | 270 |  |  | 0
VAV-7.14 |  |  |  | 1200 |  | 0 | 0
V715-1 | A243 | B | 6X6 | 70 |  |  | 0
V715-2 | A242 | F | 12X12 | 325 |  |  | 0
V715-3 | A242 | F | 12X12 | 325 |  |  | 0
VAV-7.15 |  |  |  | 720 |  | 0 | 0

## AHU-7 SGRD's (4)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-7 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V716-1 | A240 | D | 6X6 | 125 |  |  | 0
V716-2 | A241 | E | 9X9 | 200 |  |  | 0
VAV-7.16 |  |  |  | 325 |  | 0 | 0
V717-1 | A221 | E | 9X9 | 270 |  |  | 0
V717-2 | A221 | E | 9X9 | 270 |  |  | 0
V717-3 | A221 | E | 9X9 | 270 |  |  | 0
V717-4 | A221 | E | 9X9 | 270 |  |  | 0
VAV-7.17 |  |  |  | 1080 |  | 0 | 0

## AHU-8
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-8 |  | Area: CLASSROOMS
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 10 / 20X24X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame | / 213T
Horsepower / RPM | 10 / 1800 |  | Horsepower / RPM | 3.0 / 1200
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 12.0 |  | Rated Amperage / SF | 4.6
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 15000 |  | Total CFM | 15000
Min OA CFM | 2250
Fan RPM | 1956 |  | Fan RPM | 1444
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 12.0 |  | RL Amperage | 4.6
Motor B.H.P. | 15.3 |  | Motor B.H.P. | 4.5
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.21 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.25 |  | Total ESP

## AHU-8 VAV's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-8 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-8.01 | A202 | HEAT | SINGLE | 5 | 250 |  | 70 |  | 130
VAV-8.02 | A201 | HEAT | SINGLE | 10 | 995 |  | 250 |  | 500
VAV-8.03 | A203 | COOL | SINGLE | 10 | 500 |  | 150 |  | 0
VAV-8.04 | A205 | HEAT | SINGLE | 10 | 1225 |  | 310 |  | 620
VAV-8.05 | A206 | HEAT | SINGLE | 10 | 1200 |  | 300 |  | 600
VAV-8.06 | A209 | HEAT | SINGLE | 10 | 1080 |  | 270 |  | 540
VAV-8.08 | A210 | HEAT | SINGLE | 10 | 1080 |  | 270 |  | 540
VAV-8.09 | A211 | HEAT | SINGLE | 10 | 1195 |  | 300 |  | 600
VAV-8.10 | A251 | HEAT | SINGLE | 12 | 1245 |  | 470 |  | 930
VAV-8.11 | A212 | HEAT | SINGLE | 12 | 1380 |  | 350 |  | 690
VAV-8.12 | A250 | HEAT | SINGLE | 10 | 960 |  | 240 |  | 480
VAV-8.13 | A215 | HEAT | SINGLE | 10 | 1195 |  | 300 |  | 600
VAV-8.14 | A247 | HEAT | SINGLE | 10 | 960 |  | 240 |  | 480
VAV-8.15 | A246 | HEAT | SINGLE | 10 | 1080 |  | 270 |  | 540
VAV-8.16 | A216 | HEAT | SINGLE | 12 | 1830 |  | 460 |  | 920
VAV-8.17 | A219 | COOL | SINGLE | 10 | 500 |  | 150 |  | 0
VAV-8.18 | A245 | HEAT | SINGLE | 10 | 960 |  | 240 |  | 480
17635
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-8 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-8 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V802-1 | A200 | F | 12X12 | 300 |  |  | 0
V802-2 | A200 | F | 12X12 | 300 |  |  | 0
V802-3 | A201 | F | 12X12 | 395 |  |  | 0
VAV-8.02 |  |  |  | 995 |  | 0 | 0
V803-1 | A203 | B | 18X10 | 500 |  |  | 0
VAV-8.03 |  |  |  | 500 |  | 0 | 0
V804-1 | A204 | TF | 6X6 | 145 |  |  | 0
V804-2 | A205 | E | 9X9 | 270 |  |  | 0
V804-3 | A205 | E | 9X9 | 270 |  |  | 0
V804-4 | A205 | E | 9X9 | 270 |  |  | 0
V804-5 | A205 | E | 9X9 | 270 |  |  | 0
VAV-8.04 |  |  |  | 1225 |  | 0 | 0
V805-1 | A207 | TF | 6X6 | 120 |  |  | 0
V805-2 | A206 | E | 9X9 | 270 |  |  | 0
V805-3 | A206 | E | 9X9 | 270 |  |  | 0
V805-4 | A206 | E | 9X9 | 270 |  |  | 0
V805-5 | A206 | E | 9X9 | 270 |  |  | 0
VAV-8.05 |  |  |  | 1200 |  | 0 | 0
V806-1 | A209 | E | 9X9 | 270 |  |  | 0
V806-2 | A209 | E | 9X9 | 270 |  |  | 0
V806-3 | A209 | E | 9X9 | 270 |  |  | 0
V806-4 | A209 | E | 9X9 | 270 |  |  | 0
VAV-8.06 |  |  |  | 1080 |  | 0 | 0

## AHU-8 SGRD's (2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-8 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V808-1 | A210 | E | 9X9 | 270 |  |  | 0
V808-2 | A210 | E | 9X9 | 270 |  |  | 0
V808-3 | A210 | E | 9X9 | 270 |  |  | 0
V808-4 | A210 | E | 9X9 | 270 |  |  | 0
VAV-8.08 |  |  |  | 1080 |  | 0 | 0
V809-1 | A213 | TF | 6X6 | 115 |  |  | 0
V809-2 | A211 | E | 9X9 | 270 |  |  | 0
V809-3 | A211 | E | 9X9 | 270 |  |  | 0
V809-4 | A211 | E | 9X9 | 270 |  |  | 0
V809-5 | A211 | E | 9X9 | 270 |  |  | 0
VAV-8.09 |  |  |  | 1195 |  | 0 | 0
V810-1 | A249 | TF | 6X6 | 120 |  |  | 0
V810-2 | A251 | E | 9X9 | 240 |  |  | 0
V810-3 | A251 | E | 9X9 | 240 |  |  | 0
V810-4 | A252 | E | 9X9 | 165 |  |  | 0
V810-5 | A251 | E | 9X9 | 240 |  |  | 0
V810-6 | A251 | E | 9X9 | 240 |  |  | 0
VAV-8.10 |  |  |  | 1245 |  | 0 | 0
V811-1 | A212 | E | 9X9 | 270 |  |  | 0
V811-2 | A212 | E | 9X9 | 270 |  |  | 0
V811-3 | A258 | F | 12X12 | 300 |  |  | 0
V811-4 | A212 | E | 9X9 | 270 |  |  | 0
V811-5 | A212 | E | 9X9 | 270 |  |  | 0
|  |  |  | 1380 |  | 0 | 0

## AHU-8 SGRD's (3)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-8 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V812-1 | A250 | E | 9X9 | 240 |  |  | 0
V812-2 | A250 | E | 9X9 | 240 |  |  | 0
V812-3 | A250 | E | 9X9 | 240 |  |  | 0
V812-4 | A250 | E | 9X9 | 240 |  |  | 0
VAV-8.12 |  |  |  | 960 |  | 0 | 0
V813-1 | A214 | TF | 8 | 115 |  |  | 0
V813-2 | A215 | E | 9X9 | 270 |  |  | 0
V813-3 | A215 | E | 9X9 | 270 |  |  | 0
V813-4 | A215 | E | 9X9 | 270 |  |  | 0
V813-5 | A215 | E | 9X9 | 270 |  |  | 0
VAV-8.13 |  |  |  | 1195 |  | 0 | 0
V814-1 | A247 | E | 9X9 | 240 |  |  | 0
V814-2 | A247 | E | 9X9 | 240 |  |  | 0
V814-3 | A247 | E | 9X9 | 240 |  |  | 0
V814-4 | A247 | E | 9X9 | 240 |  |  | 0
VAV-8.14 |  |  |  | 960 |  | 0 | 0
V815-1 | A248 | TF | 8 | 120 |  |  | 0
V815-2 | A246 | E | 9X9 | 240 |  |  | 0
V815-3 | A246 | E | 9X9 | 240 |  |  | 0
V815-4 | A246 | E | 9X9 | 240 |  |  | 0
V815-5 | A246 | E | 9X9 | 240 |  |  | 0
VAV-8.15 |  |  |  | 1080 |  | 0 | 0

## AHU-8 SGRD's (4)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-8 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V816-1 | A258 | F | 12X12 | 300 |  |  | 0
V816-2 | A220 | C | 6X6 | 50 |  |  | 0
V816-3 | A217 | E | 9X9 | 200 |  |  | 0
V816-4 | A218 | E | 9X9 | 200 |  |  | 0
V816-5 | A216 | E | 9X9 | 270 |  |  | 0
V816-6 | A216 | E | 9X9 | 270 |  |  | 0
V816-7 | A216 | E | 9X9 | 270 |  |  | 0
V816-8 | A216 | E | 9X9 | 270 |  |  | 0
VAV-8.16 |  |  |  | 1830 |  | 0 | 0
V817-1 | A219 | B | 18X10 | 500 |  |  | 0
VAV-8.17 |  |  |  | 500 |  | 0 | 0
V818-1 |  | E | 9X9 | 240 |  |  | 0
V818-2 |  | E | 9X9 | 240 |  |  | 0
V818-3 |  | E | 9X9 | 240 |  |  | 0
V818-4 |  | E | 9X9 | 240 |  |  | 0
VAV-8.18 |  |  |  | 960 |  | 0 | 0
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!

## AHU-9
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-9 |  | Area: CLASSROOMS
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | CARRIER |  | Manufacturer | CARRIER
Model Number | 39MN |  | Model Number | 39MN
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 16X20X2 |  | No. Pre Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | / 213T |  | Motor MFG / Frame | / 145T
Horsepower / RPM | 7.5 / 1800 |  | Horsepower / RPM | 2.0 / 1800
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 9.5 |  | Rated Amperage / SF | 2.9
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 6000 |  | Total CFM | 6000
Min OA CFM | 1225
Fan RPM | 2055 |  | Fan RPM | 1981
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 9.5 |  | RL Amperage | 2.9
Motor B.H.P. | 5.6 |  | Motor B.H.P. | 1.9
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.85 |  | Total SP
CW Coil P.D.
HW Coil P.D.
HW Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.25 |  | Total ESP

## AHU-9 VAV's
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-9 VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-9.01 | B201 | HEAT | SINGLE | 8 | 500 |  | 130 |  | 250
VAV-9.02 | A195 | HEAT | SINGLE | 10 | 900 |  | 230 |  | 450
VAV-9.03 | A190 | HEAT | SINGLE | 12 | 1810 |  | 460 |  | 910
VAV-9.04 | A189 | COOL | SINGLE | 12 | 1000 |  | 300 |  | 0
VAV-9.05 | A187 | HEAT | SINGLE | 14 | 1995 |  | 500 |  | 1000
VAV-9.06 | A186 | HEAT | SINGLE | 10 | 750 |  | 190 |  | 380
6955
Note on C7: NTAB: BILLINGSLEY ONLY

## AHU-9 SGRD's (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: AHU-9 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V902-1 | A193 | E | 9X9 | 200 |  |  | 0
V902-2 | A194 | E | 9X9 | 200 |  |  | 0
V902-3 | A195 | F | 12X12 | 350 |  |  | 0
V902-4 | A192 | D | 6X6 | 100 |  |  | 0
V902-5 | PATIO | SOFFIT | 6 | 50 |  |  | 0
VAV-9.02 |  |  |  | 900 |  | 0 | 0
V903-1 | A190 | E | 9X9 | 280 |  |  | 0
V903-2 | A191 | E | 9X9 | 130 |  |  | 0
V903-3 | A190 | E | 9X9 | 280 |  |  | 0
V903-4 | A190 | E | 9X9 | 280 |  |  | 0
V903-5 | A190 | E | 9X9 | 280 |  |  | 0
V903-6 | A190 | E | 9X9 | 280 |  |  | 0
V903-7 | A190 | E | 9X9 | 280 |  |  | 0
VAV-9.03 |  |  |  | 1810 |  |  | 0
V904-1 | A189 | B | 24X14 | 1000 |  |  | 0
VAV-9.04 |  |  |  | 1000 |  | 0 | 0
V905-1 | A195 | F | 12X12 | 400 |  |  | 0
V905-2 | A187 | F | 12X12 | 370 |  |  | 0
V905-3 | A187 | F | 12X12 | 370 |  |  | 0
V905-4 | A188 | D | 6X6 | 115 |  |  | 0
V905-5 | A187 | F | 12X12 | 370 |  |  | 0
V905-6 | A187 | F | 12X12 | 370 |  |  | 0
VAV-9.05 |  |  |  | 1995 |  | 0 | 0
V906-1 | A186 | F | 12X12 | 375 |  |  | 0
V906-2 | A186 | F | 12X12 | 375 |  |  | 0
VAV-9.06 |  |  |  | 750 |  | 0 | 0

## KEF (F-1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: KEF (F-1) |  | Area: KITCHEN HOODS (B107)
Unit Data |  |  | Test Data
MFG | CAPTIVEAIRE |  |  | Design | Actual
Model Num | DU200HFA |  | CFM | 4951
Serial Num |  |  | Fan RPM | 1462
Type | CFE UPBLAST (KEF) |  | RL Voltage | 460
|  |  | RL Amperage | 6.8
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 1.5
Frame
Horsepower | 5
Motor Rpm | 1462
Phase | 3
Voltage (rated) | 460
Amperage (rated) | 6.8
Service Factor
-

## MAU (F-2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: MUA (F-2) |  | Area: KITCHEN HOODS (B107)
Unit Data |  |  | Test Data
MFG | CAPTIVEAIRE |  |  | Design | Actual
Model Num | A2-D.250-20D |  | CFM | 3960
Serial Num |  |  | SF RPM | 1587
Type | GAS FIRED MUA |  | RL Voltage | 460
Configuration | HORIZONTAL |  | RL Amperage | 4.3
No. Filters / Size |  |  | Suction ESP
No. Filters / Size |  |  | Discharge ESP
|  |  | Total ESP | 0.75
|  |  | Brake Horse Power | 2.242
Motor Data
Motor MFG
Frame
Horsepower | 3
Motor Rpm | 1587
Phase | 3
Voltage (rated) | 460
Amperage (rated) | 4.3
Service Factor

## F-3
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-3 |  | Area: DISHWASHER (B108)
Unit Data |  |  | Drive Data
MFG | COOK |  | Motor Sheave Size
Model Num | 135R OR91 |  | Motor Bore Size
Serial Num |  |  | Fan Sheave Size
Type | CRE UPBLAST |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  | No of Belts
Motor MFG |  |  | Belt Size
Frame
Horsepower | 0.5 |  | Test Data
Motor Rpm | 1725 |  |  | Design | Actual
Phase | 1 |  | CFM | 600
Voltage (rated) | 115 |  | Fan RPM | 1504
Amperage (rated) | 9.8 |  | RL Voltage | 115
Service Factor |  |  | RL Amperage | 9.8
Suction ESP
|  |  | Total ESP | 1
Brake Horse Power
-

## F-4
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: EF-4 |  |  | Area: VIS ARTS GROUP TLTS
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 90C17DEC |  |  | CFM | 600
Serial Num |  |  |  |  | Fan RPM | 1662
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.25
Frame
Horsepower |  | 0.167
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF4-1 | A194 | L | 10X10 | 300 |  |  | 0
EF4-2 | A193 | L | 10X10 | 300 |  |  | 0
|  |  |  | 600 |  | 0 | 0
-

## F-5
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-5 |  |  | Area: VIS ARTS VENTILATION
Unit Data |  |  |  |  | Drive Data
MFG |  | COOK |  |  | Motor Sheave Size
Model Num |  | 135C4B |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | CRE DNBLAST |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 0.33 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 1700
Voltage (rated) |  | 115 |  |  | Fan RPM | 1239
Amperage (rated) |  | 7.2 |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage | 7.2
Suction ESP
[5 empty] | Total ESP | 0.25
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF5-1 | A190 | P | 22X20 | 850 |  |  | 0
EF5-2 | A190 | P | 22X20 | 850 |  |  | 0
|  |  |  | 1700 |  | 0 | 0
-

## F-6
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-6 |  |  | Area: ADMIN HEALTH
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 90C17DEC |  |  | CFM | 425
Serial Num |  |  |  |  | Fan RPM | 1366
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.25
Frame
Horsepower |  | 0.167
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF6-1 | A122 | J | 8X8 | 75 |  |  | 0
EF6-2 | A123 | J | 8X8 | 75 |  |  | 0
EF6-3 | A107 | J | 8X8 | 75 |  |  | 0
EF6-4 | A106 | L | 10X10 | 200 |  |  | 0
|  |  |  | 425 |  | 0 | 0
-

## F-7
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-7 |  |  | Area: CLASSROOM GROUP TLTS
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 135C17D (VF) |  |  | CFM | 1650
Serial Num |  |  |  |  | Fan RPM | 1343
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.5
Frame
Horsepower |  | 0.5
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF7-1 | A255 | M | 12X12 | 375 |  |  | 0
EF7-2 | A254 | M | 12X12 | 375 |  |  | 0
EF7-3 | A253 | J | 8X8 | 75 |  |  | 0
EF7-4 | A184 | J | 8X8 | 75 |  |  | 0
EF7-5 | A186 | M | 12X12 | 375 |  |  | 0
EF7-6 | A185 | M | 12X12 | 375 |  |  | 0
|  |  |  | 1650 |  | 0 | 0
-

## F-8
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-8 |  |  | Area: CLASSROOM GROUP TLTS
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 100C17DEC |  |  | CFM | 675
Serial Num |  |  |  |  | Fan RPM | 1551
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.25
Frame
Horsepower |  | 0.24
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF8-1 | A220 | J | 8X8 | 75 |  |  | 0
EF8-2 | A218 | L | 10X10 | 300 |  |  | 0
EF8-3 | A217 | L | 10X10 | 300 |  |  | 0
|  |  |  | 675 |  | 0 | 0
-

## F-9
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-9 |  |  | Area: CUSTODIAN
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 70C17DEC |  |  | CFM | 120
Serial Num |  |  |  |  | Fan RPM | 1498
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.25
Frame
Horsepower |  | 0.05
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF9-1 | A243 | H | 8X8 | 120 |  |  | 0
|  |  |  | 120 |  | 0 | 0
-

## F-10
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-10 |  |  | Area: CUSTODIAN
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | 70C17DEC |  |  | CFM | 120
Serial Num |  |  |  |  | Fan RPM | 1498
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.25
Frame
Horsepower |  | 0.05
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E10-1 | A230 | H | 8X8 | 120 |  |  | 0
|  |  |  | 120 |  | 0 | 0
-

## F-11
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-11 |  | Area: K-1 TLT (A158)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GCVF-180 |  | CFM | 120
Serial Num |  |  | Fan RPM | 907
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-12
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-12 |  | Area: K-1 TLT (A164)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-13
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-13 |  | Area: K-1 TLT (A166)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-14
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-14 |  | Area: K-1 TLT (A157)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-15
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-15 |  | Area: K-1 TLT (A155)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-16
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-16 |  | Area: K-1 TLT (A168)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-17
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-17 |  | Area: K-1 TLT (A170)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-18
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-18 |  | Area: STAFF TLT (A162)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-19
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-19 |  | Area: K-1 TLT (A153)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-20
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-20 |  | Area: STAFF TLT (A161)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-21
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-21 |  | Area: K-1 TLT (A151)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-22
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-22 |  | Area: CUSTODIAN (A183)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-186 |  | CFM | 170
Serial Num |  |  | Fan RPM | 897
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-23
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-23 |  | Area: K-1 TLT (A176)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-24
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-24 |  | Area: K-1 TLT (A178)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-25
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-25 |  | Area: K-1 TLT (A147)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-26
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-26 |  | Area: K-1 TLT (A145)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-27
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-27 |  | Area: K-1 TLT (A180)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-28
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-28 |  | Area: STAFF TLT (A182)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-146 |  | CFM | 75
Serial Num |  |  | Fan RPM | 813
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-29
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-29 |  | Area: MODIFIED TLT (A141)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GCVF-180 |  | CFM | 150
Serial Num |  |  | Fan RPM | 1033
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-30
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-30 |  | Area: K-1 TLT (A143)
Unit Data |  |  | Test Data
MFG |  |  |  | Design | Actual
Model Num |  |  | CFM | 75
Serial Num |  |  | Fan RPM | 900
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor |  |  | MISSING FROM SUBMITTAL
-

## F-31
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-31 |  | Area: KILN RM VENT (A192)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GC-186 |  | CFM | 170
Serial Num |  |  | Fan RPM | 897
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-32
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-32 |  | Area: KITCHEN TLT (B114)
Unit Data |  |  | Test Data
MFG |  |  |  | Design | Actual
Model Num |  |  | CFM | 75
Serial Num |  |  | Fan RPM | 900
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor |  |  | MISSING FROM SUBMITTAL
-

## F-33
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-33 |  | Area: CUSTODIAN (B112)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | GCVF-180 |  | CFM | 130
Serial Num |  |  | Fan RPM | 948
Type | CEILING |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-34
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-34 (SUPPLY FAN) |  | Area: BOILER RM VENT (B117)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | 14XW32D17 (VF) |  | CFM | 1700
Serial Num |  |  | Fan RPM | 1659
Type | PROP WALL |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower | 0.25
Motor Rpm | 1725
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-35
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-35 |  | Area: RISER RM VENT (B118)
Unit Data |  |  | Drive Data
MFG | COOK |  | Motor Sheave Size
Model Num | 210C4B |  | Motor Bore Size
Serial Num |  |  | Fan Sheave Size
Type | CRE DNBLAST |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  | No of Belts
Motor MFG |  |  | Belt Size
Frame
Horsepower | 0.33 |  | Test Data
Motor Rpm | 1725 |  |  | Design | Actual
Phase | 1 |  | CFM | 2400
Voltage (rated) | 115 |  | Fan RPM | 535
Amperage (rated) | 7.2 |  | RL Voltage | 115
Service Factor |  |  | RL Amperage | 7.2
Suction ESP
|  |  | Total ESP | 0.25
Brake Horse Power
-

## F-36
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-36 |  | Area: ATS RM VENT (B120)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | 90C17DL (VF) |  | CFM | 200
Serial Num |  |  | Fan RPM | 1110
Type | CRE DNBLAST |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower | 0.05
Motor Rpm | 1725
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-37
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-37 |  | Area: ELEC RM VENT (B119)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | 120C17DEC |  | CFM | 1000
Serial Num |  |  | Fan RPM | 1161
Type | CRE DNBLAST |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower | 0.5
Motor Rpm | 1725
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## F-38
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: F-38 |  | Area: CUSTODIAL (B104)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | 90C17DL (VF) |  | CFM | 250
Serial Num |  |  | Fan RPM | 1227
Type | CRE DNBLAST |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower | 0.05
Motor Rpm | 1725
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## KEH-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: KEH-1 |  | Area:
Unit Data |  |  | Test Data Supply
MFG | CAPTIVEAIRE |  |  | PRELIM | FINAL
Model Num | 6024 ND-2-PSP-F |  | AK factor
Job / Serial Num | 5676413 |  | Total AK Area | 15.33
Type | TYPE I CANOPY |  | Kv factor (Vel) | 0.91
Hood length | 138 |  | Reading1 FPM
Hood Width | 60 |  | Reading2 FPM
Supply Plenum Type | PSP |  | Reading3 FPM
Supply Plenum Width | 16 |  | Reading4 FPM
Supply Plenum Length | 138 |  | Reading5 FPM
Reading6 FPM
Test Data Exhaust |  |  | Reading7 FPM
| PRELIM | FINAL | Reading8 FPM
Filter Type | CAPTRATE |  | Reading9 FPM
Filter Size 1 | 16X16 |  | Reading10 FPM
Filter Qty 1 | 8 |  | Reading11 FPM
Filter AK factor size 1 | 1.62 |  | Reading12 FPM
Filter Total AK Area | 12.96 |  | Reading13 FPM
Filter1 FPM |  |  | Reading14 FPM
Filter2 FPM |  |  | Ave FPM(corr)
Filter3 FPM |  |  | CFM | 2070
Filter4 FPM
Filter5 FPM |  |  | Performance Data
Filter6 FPM |  |  |  | Design | Actual
Filter7 FPM |  |  | Exh-Supply Net CFM | 518
Filter8 FPM |  |  | Smoke Generation Type
Filter9 FPM |  |  | Cooking Equip Heat On
Filter Ave FPM |  |  | Hood Capture %
CFM | 2588 |  | Ambient Room Temp
100% override functional
Cooking Equipment |  |  | General
Item 1 |  |  | Third Party Witness
Item 2 |  |  | Third Party Company
Item 3 |  |  | Tech Witness
Item 4 |  |  | Tech Company
Item 5 |  |  | Code Official Witness

## KEH-2
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: KEH-2 |  | Area:
Unit Data |  |  | Test Data Supply
MFG | CAPTIVEAIRE |  |  | PRELIM | FINAL
Model Num | 6024 ND-2-PSP-F |  | AK factor
Job / Serial Num | 5676413 |  | Total AK Area | 15.33
Type | TYPE I CANOPY |  | Kv factor (Vel) | 0.91
Hood length | 126 |  | Reading1 FPM
Hood Width | 60 |  | Reading2 FPM
Supply Plenum Type | PSP |  | Reading3 FPM
Supply Plenum Width | 16 |  | Reading4 FPM
Supply Plenum Length | 138 |  | Reading5 FPM
Reading6 FPM
Test Data Exhaust |  |  | Reading7 FPM
| PRELIM | FINAL | Reading8 FPM
Filter Type | CAPTRATE |  | Reading9 FPM
Filter Size 1 | 16X16 |  | Reading10 FPM
Filter Qty 1 | 8 |  | Reading11 FPM
Filter AK factor size 1 | 1.62 |  | Reading12 FPM
Filter Total AK Area | 11.34 |  | Reading13 FPM
Filter1 FPM |  |  | Reading14 FPM
Filter2 FPM |  |  | Ave FPM(corr)
Filter3 FPM |  |  | CFM | 1890
Filter4 FPM
Filter5 FPM |  |  | Performance Data
Filter6 FPM |  |  |  | Design | Actual
Filter7 FPM |  |  | Exh-Supply Net CFM | 470
Filter8 FPM |  |  | Smoke Generation Type
Filter9 FPM |  |  | Cooking Equip Heat On
Filter Ave FPM |  |  | Hood Capture %
CFM | 2360 |  | Ambient Room Temp
100% override functional
Cooking Equipment |  |  | General
Item 1 |  |  | Third Party Witness
Item 2 |  |  | Third Party Company
Item 3 |  |  | Tech Witness
Item 4 |  |  | Tech Company
Item 5 |  |  | Code Official Witness

## CH-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: CH-1 |  |  | Asset: CHILLER 2
UNIT DATA |  |  | UNIT DATA
Unit Description | AIR COOLED CHILLER |  | Unit Description
Manufacturer | CARRIER |  | Manufacturer
Model Number | 30XV250S |  | Model Number
Serial Number |  |  | Serial Number
EVAPORATOR DATA | Design | Actual | EVAPORATOR DATA | Design | Actual
Flow GPM | 517.3 |  | Flow GPM
Pressure Drop | 14.2 |  | Pressure Drop
Asset: CHILLER 3 |  |  | Asset: CHILLER 4
UNIT DATA |  |  | UNIT DATA
Unit Description |  |  | Unit Description
Manufacturer |  |  | Manufacturer
Model Number |  |  | Model Number
Serial Number |  |  | Serial Number
EVAPORATOR DATA | Design | Actual | EVAPORATOR DATA | Design | Actual
Flow GPM |  |  | Flow GPM
Pressure Drop |  |  | Pressure Drop

## B-1 & B-2
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: BOILER |  | Service: HOT WATER
Unit Data | B-1 |  | B-1 |  | Boiler 3
Manufacturer | PEERLESS |  | PEERLESS
Model Number | LC-11-W |  | LC-11-W
Serial Number
Test Data | Design | Actual | Design | Actual | Design | Actual
Water Flow GPM
Water Press. Drop

## CWP-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: CWP-1
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-5X4X8-4P-7.5 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CHILLER LOOP | Valve Open GPM
Pump RPM | 1800 | Valve Open Diff (ft)
GPM/Head | 517 / 34 | Discharge Pressure (ft)
Impellar Diameter | 7.01 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 213TC | RL Voltage | 460
Horsepower | 7.5 | RL Amperage
Motor RPM | 1770 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CWP-2
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: CWP-2
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-5X4X8-4P-7.5 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CHILLER LOOP | Valve Open GPM
Pump RPM | 1800 | Valve Open Diff (ft)
GPM/Head | 517 / 34 | Discharge Pressure (ft)
Impellar Diameter | 7.01 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 213TC | RL Voltage | 460
Horsepower | 7.5 | RL Amperage
Motor RPM | 1770 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## BCWP-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: BCWP-1
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-4X3X6-2P-20 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CHILLED WATER LOOP | Valve Open GPM
Pump RPM | 3600 | Valve Open Diff (ft)
GPM/Head | 517 / 98 | Discharge Pressure (ft)
Impellar Diameter | 5.75 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 254TC | RL Voltage | 460
Horsepower | 20 | RL Amperage
Motor RPM | 3560 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## BCWP-2
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: BCWP-1
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-4X3X6-2P-20 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | CHILLED WATER LOOP | Valve Open GPM
Pump RPM | 3600 | Valve Open Diff (ft)
GPM/Head | 517 / 98 | Discharge Pressure (ft)
Impellar Diameter | 5.75 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 254TC | RL Voltage | 460
Horsepower | 20 | RL Amperage
Motor RPM | 3560 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## BHWP-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: BHWP-1
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-1.5X1X6-2P-5 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | HOT WATER LOOP | Valve Open GPM
Pump RPM | 3600 | Valve Open Diff (ft)
GPM/Head | 82 / 93 | Discharge Pressure (ft)
Impellar Diameter | 5.17 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 182TC | RL Voltage | 460
Horsepower | 5 | RL Amperage
Motor RPM | 3530 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## BHWP-2
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: BHWP-2
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-1.5X1X6-2P-5 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | HOT WATER LOOP | Valve Open GPM
Pump RPM | 3600 | Valve Open Diff (ft)
GPM/Head | 82 / 93 | Discharge Pressure (ft)
Impellar Diameter | 5.17 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 182TC | RL Voltage | 460
Horsepower | 5 | RL Amperage
Motor RPM | 3530 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HWP-1
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: HWP-1
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-5X4X8-4P-7.5 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | BOILER LOOP | Valve Open GPM
Pump RPM | 1800 | Valve Open Diff (ft)
GPM/Head | 79 / 27 | Discharge Pressure (ft)
Impellar Diameter | 5.54 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 145JM | RL Voltage | 460
Horsepower | 1.5 | RL Amperage
Motor RPM | 1760 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HWP-2
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: HWP-2
Unit Data |  | Test Data
| Actual |  | Design | Actual
MFG | ARMSTRONG | Pump Off Pressure (psi)
Model Num | 4030-5X4X8-4P-7.5 | Pump Dead Head (ft)
Serial Num |  | Act. Impellar Dia (in)
Service | BOILER LOOP | Valve Open GPM
Pump RPM | 1800 | Valve Open Diff (ft)
GPM/Head | 79 / 27 | Discharge Pressure (ft)
Impellar Diameter | 5.54 | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  | Final GPM
| Actual | Motor Frequency (HZ)
Motor MFG |  | System Set Point
Frame | 145JM | RL Voltage | 460
Horsepower | 1.5 | RL Amperage
Motor RPM | 1760 | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CHW CS (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: CHW CIRCUIT SETTERS |  |  |  | Service: CHILLED WATER
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design
AHU-9 | B201 |  |  |  |  | 45.4 |  |  |  |  | CS-1
AHU-5 | B201 |  |  |  |  | 94.5 |  |  |  |  | CS-2
AHU-6 | B201 |  |  |  |  | 80.2 |  |  |  |  | CS-3
AHU-8 | A202 |  |  |  |  | 114 |  |  |  |  | CS-4
AHU-4 | A280 |  |  |  |  | 45.4 |  |  |  |  | CS-5
AHU-3 | A280 |  |  |  |  | 46.9 |  |  |  |  | CS-6
AHU-2 | A148 |  |  |  |  | 68.8 |  |  |  |  | CS-7
AHU-7 | A231 |  |  |  |  | 114 |  |  |  |  | CS-8
AHU-1 | A159 |  |  |  |  | 74.2 |  |  |  |  | CS-9

## HW CS (1)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: HW CIRCUIT SETTERS |  |  |  | Service: HOT WATER
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design
AHU-9 | B201 |  |  |  |  | 6 |  |  |  |  | CS-1
VAV-9.1 | B201 |  |  |  |  | 1 |  |  |  |  | CS-2
AHU-5 PREHEAT | B201 |  |  |  |  | 10.2 |  |  |  |  | CS-3
AHU-5 REHEAT | B201 |  |  |  |  | 12.7 |  |  |  |  | CS-4
AHU-6 PREHEAT | B201 |  |  |  |  | 7.9 |  |  |  |  | CS-5
AHU-6 REHEAT | B201 |  |  |  |  | 10.1 |  |  |  |  | CS-6
VAV-9.2 | A195 |  |  |  |  | 1 |  |  |  |  | CS-7
VAV-9.3 | A193 |  |  |  |  | 1.5 |  |  |  |  | CS-8
VAV-9.5 | A195 |  |  |  |  | 1.7 |  |  |  |  | CS-9
VAV-9.6 | A187 |  |  |  |  | 1 |  |  |  |  | CS-10
VAV-8.06 | A209 |  |  |  |  | 1 |  |  |  |  | CS-11
VAV-8.04 | A205 |  |  |  |  | 1.1 |  |  |  |  | CS-12
VAV-8.05 | A206 |  |  |  |  | 1 |  |  |  |  | CS-13
VAV-8.02 | A200 |  |  |  |  | 1 |  |  |  |  | CS-14
VAV-8.01 | A202 |  |  |  |  | 1 |  |  |  |  | CS-15
AHU-8 | A202 |  |  |  |  | 12.5 |  |  |  |  | CS-16
VAV-4.07 | A130 |  |  |  |  | 1 |  |  |  |  | CS-17
VAV-4.06 | A130 |  |  |  |  | 1 |  |  |  |  | CS-18
VAV-4.08 | A131 |  |  |  |  | 1 |  |  |  |  | CS-19
VAV-3.16 | HALL |  |  |  |  | 1 |  |  |  |  | CS-20
VAV-4.05 | A132 |  |  |  |  | 1 |  |  |  |  | CS-21
VAV-3.06 | A116 |  |  |  |  | 1 |  |  |  |  | CS-22
VAV-4.02 | A134 |  |  |  |  | 1 |  |  |  |  | CS-23
VAV-4.09 | A280 |  |  |  |  | 1 |  |  |  |  | CS-24
VAV-4.04 | A130 |  |  |  |  | 1.4 |  |  |  |  | CS-25
VAV-4.03 | A130 |  |  |  |  | 1 |  |  |  |  | CS-26
VAV-4.01 | A135 |  |  |  |  | 1 |  |  |  |  | CS-27
VAV-3.01 | A124 |  |  |  |  | 1 |  |  |  |  | CS-28
VAV-3.03 | A115 |  |  |  |  | 1 |  |  |  |  | CS-29
VAV-3.05 | A114 |  |  |  |  | 1 |  |  |  |  | CS-30
VAV-3.14 | HALL |  |  |  |  | 1 |  |  |  |  | CS-31
VAV-3.13 | A105 |  |  |  |  | 1 |  |  |  |  | CS-32
VAV-3.15 | A105 |  |  |  |  | 1 |  |  |  |  | CS-33
VAV-3.17 | A105 |  |  |  |  | 1 |  |  |  |  | CS-34
VAV-3.12 | A108 |  |  |  |  | 1 |  |  |  |  | CS-35
VAV-3.11 | A106 |  |  |  |  | 1 |  |  |  |  | CS-36
VAV-3.10 | A111 |  |  |  |  | 1 |  |  |  |  | CS-37
VAV-3.08 | A112 |  |  |  |  | 1 |  |  |  |  | CS-38

## HW CS (2)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: HW CIRCUIT SETTERS |  |  |  | Service: HOT WATER
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design
VAV-3.09 | A121 |  |  |  |  | 1 |  |  |  |  | CS-39
VAV-3.07 | A113 |  |  |  |  | 1 |  |  |  |  | CS-40
AHU-4 | A280 |  |  |  |  | 5.3 |  |  |  |  | CS-41
AHU-3 | A280 |  |  |  |  | 8.4 |  |  |  |  | CS-42
VAV-8.08 | A210 |  |  |  |  | 1 |  |  |  |  | CS-43
VAV-8.10 | A251 |  |  |  |  | 1.6 |  |  |  |  | CS-44
VAV-8.09 | A211 |  |  |  |  | 1 |  |  |  |  | CS-45
VAV-8.11 | A212 |  |  |  |  | 1.2 |  |  |  |  | CS-46
VAV-8.12 | A250 |  |  |  |  | 1 |  |  |  |  | CS-47
VAV-8.13 | A215 |  |  |  |  | 1 |  |  |  |  | CS-48
VAV-8.14 | A247 |  |  |  |  | 1 |  |  |  |  | CS-49
VAV-8.15 | A246 |  |  |  |  | 1 |  |  |  |  | CS-50
VAV-8.16 | A216 |  |  |  |  | 1.5 |  |  |  |  | CS-51
VAV-8.18 | A245 |  |  |  |  | 1 |  |  |  |  | CS-52
VAV-2.03 | A146 |  |  |  |  | 1 |  |  |  |  | CS-53
VAV-2.01 | A148 |  |  |  |  | 1 |  |  |  |  | CS-54
AHU-2 | A148 |  |  |  |  | 6.7 |  |  |  |  | CS-55
VAV-2.02 | A175 |  |  |  |  | 1 |  |  |  |  | CS-56
VAV-2.05 | A177 |  |  |  |  | 1 |  |  |  |  | CS-57
VAV-2.06 | A144 |  |  |  |  | 1.2 |  |  |  |  | CS-58
VAV-2.08 | A142 |  |  |  |  | 1.2 |  |  |  |  | CS-59
VAV-2.07 | A179 |  |  |  |  | 1 |  |  |  |  | CS-60
VAV-2.09 | A181 |  |  |  |  | 1 |  |  |  |  | CS-61
VAV-2.11 | A181 |  |  |  |  | 1.2 |  |  |  |  | CS-62
VAV-2.10 | A140 |  |  |  |  | 1 |  |  |  |  | CS-63
VAV-3.18 | A104 |  |  |  |  | 1 |  |  |  |  | CS-64
VAV-7.16 | A240 |  |  |  |  | 1 |  |  |  |  | CS-65
VAV-7.17 | A221 |  |  |  |  | 1 |  |  |  |  | CS-66
VAV-7.15 | A242 |  |  |  |  | 1 |  |  |  |  | CS-67
VAV-7.14 | A222 |  |  |  |  | 1 |  |  |  |  | CS-68
VAV-7.12 | A239 |  |  |  |  | 1 |  |  |  |  | CS-69
VAV-7.11 | A223 |  |  |  |  | 1.1 |  |  |  |  | CS-70
VAV-7.10 | A238 |  |  |  |  | 1 |  |  |  |  | CS-71
VAV-7.09 | A224 |  |  |  |  | 1 |  |  |  |  | CS-72
VAV-7.08 | A237 |  |  |  |  | 1 |  |  |  |  | CS-73
VAV-7.07 | A227 |  |  |  |  | 1.1 |  |  |  |  | CS-74
VAV-7.06 | A234 |  |  |  |  | 1 |  |  |  |  | CS-75
VAV-7.04 | A233 |  |  |  |  | 1 |  |  |  |  | CS-76

## HW CS (3)
National TAB
Project: CMS Hidden Valley, Grier, Newell Relief School
Address: 7515 The Plaza Charlotte, NC 28215
Asset: HW CIRCUIT SETTERS |  |  |  | Service: HOT WATER
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design | MY NOTES DON'T PRINT
VAV-7.05 | A228 |  |  |  |  | 1 |  |  |  |  | CS-77
VAV-7.03 | A229 |  |  |  |  | 1.2 |  |  |  |  | CS-78
VAV-7.02 | A232 |  |  |  |  | 1.2 |  |  |  |  | CS-79
VAV-1.01 | A159 |  |  |  |  | 1 |  |  |  |  | CS-80
AHU-1 | A159 |  |  |  |  | 8.4 |  |  |  |  | CS-81
VAV-1.02 | A163 |  |  |  |  | 1.2 |  |  |  |  | CS-82
VAV-1.03 | A156 |  |  |  |  | 1.3 |  |  |  |  | CS-83
VAV-1.04 | A165 |  |  |  |  | 1 |  |  |  |  | CS-84
VAV-1.05 | A154 |  |  |  |  | 1 |  |  |  |  | CS-85
VAV-1.06 | A167 |  |  |  |  | 1 |  |  |  |  | CS-86
VAV-1.07 | A152 |  |  |  |  | 1.3 |  |  |  |  | CS-87
VAV-1.08 | A169 |  |  |  |  | 1 |  |  |  |  | CS-88
VAV-1.09 | A169 |  |  |  |  | 1 |  |  |  |  | CS-89
VAV-1.11 | A150 |  |  |  |  | 1 |  |  |  |  | CS-90
VAV-7.01 | A231 |  |  |  |  | 1 |  |  |  |  | CS-91
AHU-7 | A231 |  |  |  |  | 12.5 |  |  |  |  | CS-92