## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BOH | 4500 | 4538 | 3800 | 3803 | 700 | 735 | 15.56% | 16.2%
RTU-2 | DELI | 3400 | 3734 | 3020 | 3329 | 380 | 405 | 11.18% | 10.85%
RTU-3 | RETAIL | 2400 | 376 | 2200 | 162 | 200 | 214 | 8.333% | 56.91%
EF-1 | RESTROOMS | [12 empty] | 375 | 365
EF-2 | BOH | [12 empty] | 400 | 384
EF-3 | TRASH ROOM | [12 empty] | 200 | 202
TOTALS |  | 10300 | 8648 | 9020 | 7294 | 1280 | 1354 |  |  | 0 | 0 | 0 | 0 | 975 | 951
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1280 | 1354 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 975 | 951 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 305 | 403 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
UNABLE TO RECORD BUILDING PRESSURE. ALL UNITS COULD NOT BE RUN AT THE SAME TIME FOR TEST TO BE TAKEN. EXHAUST FAN DISCONNECTED FROM TEMP POWER WHEN ELECTRICIANS LEFT SITE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0