## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | FRONT DINING | 2400 | 1977 | 1700 | 1372 | 700 | 605 | 29.17% | 30.6%
AHU-2 | DINING | 3000 | 2952 | 2220 | 2164 | 780 | 788 | 26% | 26.69%
AHU-3 | KITHCEN | 3000 | 2873 | 2790 | 2652 | 210 | 221 | 7% | 7.692%
KEF 1 | FRYER | [10 empty] | 648 | 652
KEF 2 | KETTLE | [10 empty] | 1210 | 841
KEF 3 | DISH | [10 empty] | 500 | 0
KMUA | KETTLE | [8 empty] | 1080 | 1114
EF-1 | WOMEN'S RR | [12 empty] | 80 | 82
EF-2 | MEN'S RR | [12 empty] | 80 | 77
TOTALS |  | 8400 | 7802 | 6710 | 6188 | 1690 | 1614 |  |  | 1080 | 1114 | 2358 | 1493 | 160 | 159
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2770 | 2728 |  | FRONT |  | 0.001" | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2518 | 1652 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 252 | 1076 |  | REAR |  | 0.002" | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.006 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0