## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3500 | 4049 | 2700 | 3311 | 800 | 738 | 22.86% | 18.23%
RTU-2 | KITCHEN | 5200 | 5168 | 4900 | 4856 | 300 | 312 | 5.769% | 6.037%
MUA-1 | COOKLINE | [8 empty] | 3045 | 3098
KEF-1 | HOOD 1 | [10 empty] | 2015 | 2016
KEF-2 | HOOD 2 | [10 empty] | 1794 | 1790
EF-1 | RESTROOM | [12 empty] | 300 | 302
TOTALS |  | 8700 | 9217 | 7600 | 8167 | 1100 | 1050 |  |  | 3045 | 3098 | 3809 | 3806 | 300 | 302
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4145 | 4148 |  | FRONT |  | 0.0009 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4109 | 4108 |  | SIDE |  | 0.0008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 36 | 40 |  | REAR |  | 0.0005 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00073333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 3345 | 3410
TOTAL KITCHEN EXHAUST |  | 3809 | 3806
NET AIRFLOW |  | -464 | -396
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0