## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3000 | 2992 | 2500 | 2477 | 500 | 515 | 16.67% | 17.21%
RTU-2 | DINING | 3200 | 3076 | 2200 | 2093 | 1000 | 983 | 31.25% | 31.96%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1871
EF-1 | KITCHEN HOOD | [10 empty] | 1600 | 1515
EF-2 | KITCHEN HOOD | [10 empty] | 1600 | 1514
EF-3 | RESTROOM | [12 empty] | 150 | 145
TOTALS |  | 6200 | 6068 | 4700 | 4570 | 1500 | 1498 |  |  | 1950 | 1871 | 3200 | 3029 | 150 | 145
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3369 |  | FRONT |  | 0.00629 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3350 | 3174 |  | SIDE |  | 0.00442 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 195 |  | REAR |  | 0.00261 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00444 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250