## RTU-1
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-1 |  | Area: OFFICE
Unit Data |  |  | Test Data
Manufacturer | CARRIER |  |  | Design | Actual
Model Num | 50TM-008-P-501--- |  | SF CFM | 2875 | 2312
Serial Num | 2403630411 |  | SF RPM |  | 908
Configuration | VERTICAL |  | RA CFM | 2475 | 1254
Num OA Filters | - |  | OA CFM | 400 | -
OA Filter Size | - |  | RL VOLTAGE |  | 206/208.4/208.2
Num PreFilter | 4 |  | RL AMPERAGE |  | 4.9/4.9/4.9
PreFilter Size | 20X16X2 |  | OA Damper Position |  | 0% OPEN
Brake Horsepower
Motor Data |  |  | Performance Data
Motor MFG | MARATHON |  |  | Design | Actual
Frame | 56Y |  | Fan Suction SP |  | -1.02"
Horsepower | NL |  | Fan Discharge SP |  | 0.9"
Motor RPM | 1725 |  | Fan Total SP |  | 1.92"
Phase | 3 |  | CX Coil PD * |  | -
Rated Voltage | 208 |  | Pre Filter PD *Combined |  | 0.2"
Rated Amperage | 5.2 |  | Total ESP |  | 1.78"
Service Factor | 1.15
Drive Data
Motor Sheave Size / Bore | 1VL44/0.625"
Fan Sheave Size / Bore | AM74/1"
Belt CL Distance | 17.75"
No. Belts / Size | 1/AX51

## RTU-1 VAV's
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: AHU-1 VAV's
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-1.1 | LOBBY | A | 24X12 | 750 | 599 | 150 | 144
VAV-1.2 | LOBBY | A | 24X12 | 825 | 650 | 165 | 171
VAV-1.3 | OFFICE | A | 10 | 300 | 247 | 60 | 57
VAV-1.4 | OFFICE | A | 10 | 300 | 239 | 60 | 59
VAV-1.5 | OFFICE | A | 14X12 | 450 | 375 | 90 | 96
VAV-1.6 | OFFICE | A | 10 | 250 | 202 | 50 | 51
|  |  |  | 2875 | 2312
NOTES: | DESIGN MIN CFM IS 20% OF DESIGN MAX CFM
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU-1 GRD's
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: AHU-1 SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1.1-1 | LOBBY | A | 10 | 250 | 159 | 202 | 0.808
1.1-2 | LOBBY | A | 10 | 250 | 0 | 201 | 0.804
1.1-3 | LOBBY | A | 10 | 250 | 155 | 196 | 0.784
VAV-1.1 |  |  |  | 750 |  | 599 | 0.79867
1.2-1 | LOBBY | A | 10 | 300 | 231 | 240 | 0.8
1.2-2 | LOBBY | A | 10 | 225 | 201 | 174 | 0.77333
1.2-3 | LOBBY | A | 10 | 300 | 188 | 236 | 0.78667
VAV-1.2 |  |  |  | 825 |  | 650 | 0.78788
1.3-1 | OFFICE | A | 10 | 300 | 315 | 247 | 0.82333
VAV-1.3 |  |  |  | 300 |  | 247 | 0.82333
1.4-1 | OFFICE | A | 10 | 300 | 366 | 239 | 0.79667
VAV-1.4 |  |  |  | 300 |  | 239 | 0.79667
1.5-1 | DATA ROOM | A | 8 | 150 | 154 | 135 | 0.9
1.5-2 | OFFICE | A | 10 | 300 | 218 | 240 | 0.8
VAV-1.5 |  |  |  | 450 |  | 375 | 0.83333
1.6-1 | OFFICE | A | 10 | 250 | 277 | 202 | 0.808
VAV-1.6 |  |  |  | 250 |  | 202 | 0.808
Asset: AHU-1 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R1-1 | OFFICE | B | 10 | 300 | 225 | 165 | 0.55
R1-2 | LOBBY | B | 14 | 825 | 325 | 377 | 0.45697
R1-3 | LOBBY | B | 14 | 750 | 226 | 278 | 0.37067
R1-4 | OFFICE | B | 10 | 300 | 149 | 168 | 0.56
R1-5 | OFFICE | B | 10 | 300 | 138 | 152 | 0.50667
R1-6 | OFFICE | B | 10 | 250 | 191 | 190 | 0.76
RTU-1 |  |  |  | 2725 | 1254 | 1330 | 0.48807

## RTU-2
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-2 |  | Area: OFFICE
Unit Data |  |  | Test Data
Manufacturer | CARRIER |  |  | Design | Actual
Model Num | 50TFF005-A-511-- |  | SF CFM | 1600 | 1139
Serial Num | 1903G20127 |  | SF RPM |  | 1024
Configuration | VERTICAL |  | RA CFM | 1250 | 1008
Num OA Filters | - |  | OA CFM | 350 | -
OA Filter Size | - |  | RL VOLTAGE |  | 208.4
Num PreFilter | 2 |  | RL AMPERAGE |  | 2.4
PreFilter Size | 16X25X2 |  | OA Damper Position |  | -
|  |  | Brake Horsepower |  | 0.49
Motor Data |  |  | Performance Data
Motor MFG | GE MOTORS |  |  | Design | Actual
Frame | NL |  | Fan Suction SP |  | -0.5"
Horsepower | 1 |  | Fan Discharge SP |  | 0.25"
Motor RPM | 1620 |  | Fan Total SP |  | 0.75"
Phase | 1 |  | CX Coil PD * |  | -
Rated Voltage | 208 |  | Pre Filter PD *Combined |  | 0.15"
Rated Amperage | 4.9 |  | Total ESP |  | 0.60"
Service Factor | 1
Drive Data
Motor Sheave Size / Bore | 1VL34/0.5"
Fan Sheave Size / Bore | 4.375"/0.625"
Belt CL Distance | 13.375"
No. Belts / Size | 1/A36

## RTU-2 GRD's
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-2 SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-1 | RECEPTION | A | 10 | 225 | 227 | 225 | 1
2-2 | RECEPTION | A | 10 | 225 | 214 | 246 | 1.0933
2-3 | OFFICE | A | 8 | 125 | 201 | 119 | 0.952
2-4 | OFFICE | A | 8 | 125 | 206 | 125 | 1
2-5 | OFFICE | A | 8 | 175 | 170 | 186 | 1.0629
2-6 | OFFICE | A | 8 | 140 | 118 | 132 | 0.94286
2-7 | OFFICE | A | 8 | 140 | 96 | 103 | 0.73571
RTU-2* |  |  |  | 1155 |  | 1136 | 0.98355
*NOTES: | SUPPLY DUCT CONTINUES INTO A "NO WORK" AREA. ASSUME ADDITIONAL SGRD's.
Asset: RTU-2 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R2-1 | OFFICE | B | 8 | 125 | 250 | 110 | 0.88
R2-2 | OFFICE | B | 8 | 175 | 124 | 150 | 0.85714
R2-3 | OFFICE | B | 8 | 125 | 167 | 106 | 0.848
R2-4 | HALLWAY | B | 14 | 700 | 441 | 525 | 0.75
R2-5 | OFFICE | B | 8 | 125 | 78 | 106 | 0.848
RTU-2 |  |  |  | 1250 |  | 997 | 0.7976

## RTU-5
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-5 |  | Area: OFFICE & CONFERENCE
Unit Data |  |  | Test Data
Manufacturer | CARRIER |  |  | Design | Actual
Model Num | 50TJ-006---501 |  | SF CFM | 2010 | 1240
Serial Num | 3598G21685 |  | SF RPM |  | DD
Configuration | VERTICAL |  | RA CFM | 1650 | -
Num OA Filters | 1 |  | OA CFM | 360 | -
OA Filter Size | 25X8X1 |  | RL VOLTAGE |  | 207.4
Num PreFilter | 2 |  | RL AMPERAGE |  | 4.2
PreFilter Size | 15.5X25X2 |  | OA Damper Position |  | 0.625" OPEN
|  |  | Brake Horsepower |  | 0.71
Motor Data |  |  | Performance Data
Motor MFG | NA |  |  | Design | Actual
Frame | NL |  | Fan Suction SP |  | -0.82"
Horsepower | 1 |  | Fan Discharge SP |  | 0.29"
Motor RPM | 1040 |  | Fan Total SP |  | 1.11"
Phase | 1 |  | CX Coil PD * |  | -
Rated Voltage | 208 |  | Pre Filter PD *Combined |  | 0.4"
Rated Amperage | 5.9 |  | Total ESP |  | 0.71"
Service Factor | 1
Drive Data
Motor Sheave Size / Bore | DD
Fan Sheave Size / Bore | DD
Belt CL Distance | DD
No. Belts / Size | DD

## RTU-5 VAV's
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: AHU-5 VAV's
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
VAV-5.1 | OFFICE | A | 16 | 1050 | 636 | 210 | 217
VAV-5.2 | CONFERENCE | LD | 16 | 960 | 604 | 192 | 187
2010
NOTES: | DESIGN MIN CFM IS 20% OF DESIGN MAX CFM
Note on C7: NTAB: BILLINGSLEY ONLY

## RTU-5 GRD's
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-5 SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
5.1-1 | OFFICE | A | 8 | 200 | 173 | 120 | 0.6
5.1-2 | OFFICE | A | 8 | 200 | 125 | 123 | 0.615
5.1-3 | OFFICE | A | 8 | 200 | 179 | 119 | 0.595
5.1-4 | HALLWAY | A | 8 | 150 | 161 | 88 | 0.58667
5.1-5 | RECEPTION | A | 10 | 300 | 185 | 186 | 0.62
VAV-5.1 |  |  |  | 1050 |  | 636 | 0.60571
5.2-1 |  | C | 10 | 320 | 160 | 215 | 0.67188
5.2-2 |  | C | 10 | 320 | 130 | 192 | 0.6
5.2-3 |  | C | 10 | 320 | 129 | 197 | 0.61562
VAV-5.2 |  |  |  | 960 |  | 604 | 0.62917
Asset: RTU-5 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R1-1 | OFFICE | B | 10 | 200 |  |  | 0
R1-2 | OFFICE | B | 10 | 200 |  |  | 0
R1-3 | OFFICE | B | 10 | 200 |  |  | 0
R1-4 | OFFICE | B | 16 | 1050 |  |  | 0
RTU-5 |  |  |  | 1650 |  | 0 | 0
NOTES: RETURN IS TAKEN FROM PLENUM ABOVE CEILING

## RTU-6
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-6 |  | Area: OFFICE
Unit Data |  |  | Test Data
Manufacturer | CARRIER |  |  | Design | Actual
Model Num | 50GS-024---301 |  | SF CFM | 800 | 688
Serial Num | 1803011853 |  | SF RPM |  | DD
Configuration | HORIZONTAL |  | RA CFM | 800 | 607
Num OA Filters | - |  | OA CFM | 0 | 0
OA Filter Size | - |  | RL VOLTAGE |  | 207.7
Num PreFilter | NA |  | RL AMPERAGE |  | 1.8
PreFilter Size | NA |  | OA Damper Position |  | -
|  |  | Brake Horsepower |  | -
Motor Data |  |  | Performance Data
Motor MFG | NA |  |  | Design | Actual
Frame | NA |  | Fan Suction SP |  | -0.51"
Horsepower | NA |  | Fan Discharge SP |  | 0.19"
Motor RPM | NA |  | Fan Total SP |  | 0.7"
Phase | 1 |  | CX Coil PD * |  | -
Rated Voltage | 208 |  | Pre Filter PD *Combined |  | 0.25"
Rated Amperage | 2 |  | Total ESP |  | 0.45"
Service Factor | 1
Drive Data
Motor Sheave Size / Bore | DD
Fan Sheave Size / Bore | DD
Belt CL Distance | DD
No. Belts / Size | DD

## RTU-6 GRD's
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-6 SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
6-1 | OFFICE | A | 8 | 200 | 165 | 165 | 0.825
6-2 | OFFICE | A | 8 | 200 | 171 | 171 | 0.855
6-3 | OFFICE | A | 8 | 200 | 179 | 179 | 0.895
6-4 | OFFICE | A | 8 | 200 | 173 | 173 | 0.865
RTU-6 |  |  |  | 800 |  | 688 | 0.86
Asset: RTU-6 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R6-1 | OFFICE | B | 8 | 200 | 156 | 156 | 0.78
R6-2 | OFFICE | B | 8 | 200 | 138 | 138 | 0.69
R6-3 | OFFICE | B | 8 | 200 | 154 | 154 | 0.77
R6-4 | OFFICE | B | 8 | 200 | 149 | 149 | 0.745
RTU-6 |  |  |  | 800 |  | 597 | 0.74625

## RTU-7
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-7 |  | Area:
UNIT DATA |  |  | Test Data
Manufacturer | CARRIER |  |  | Design | Actual
Model Num | 50JS-030---301 |  | SF CFM | 1000 | 855
Serial Num | 3213G11529 |  | SF RPM |  | -
Configuration | HORIZONTAL |  | RA CFM | 1000 | 733
Num OA Filters | - |  | OA CFM | 0 | -
OA Filter Size | - |  | RL VOLTAGE |  | 207.3
Num PreFilter | 2 |  | RL AMPERAGE |  | 1.7
PreFilter Size | 19.5X25X2 |  | OA Damper Position |  | -
PreFilter Size 2 | 19.5X9.5X2 |  | Brake Horsepower |  | -
Motor Data |  |  | Performance Data
Motor MFG | NA |  |  | Design | Actual
Frame | NA |  | Fan Suction SP |  | -0.34
Horsepower | NA |  | Fan Discharge SP |  | 0.15"
Motor RPM | NA |  | Fan Total SP |  | 0.49"
Phase | 1 |  | CX Coil PD * |  | -
Rated Voltage | 208 |  | Pre Filter PD *Combined |  | 0.27"
Rated Amperage | 2 |  | Total ESP |  | 0.22"
Service Factor | 1
Drive Data
Motor Sheave Size / Bore | DD
Fan Sheave Size / Bore | DD
Belt CL Distance | DD
No. Belts / Size | DD

## RTU-7 GRD's
National TAB
Project: Starr Electric
Address: 1808 Norland Road Charlotte, NC
Asset: RTU-7 SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
7-1 | OFFICE | A | 10 | 300 | 204 | 204 | 0.68
7-2 | RECEPTION | A | 8 | 200 | 235 | 235 | 1.175
7-3 | OFFICE | A | 8 | 160 | 136 | 136 | 0.85
7-4 | OFFICE | A | 8 | 160 | 130 | 130 | 0.8125
7-5 | OFFICE | A | 8 | 160 | 150 | 150 | 0.9375
RTU-7 |  |  |  | 980 |  | 855 | 0.87245
Asset: RTU-7 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R7-1 | OFFICE | B | 10 | 300 | 251 | 251 | 0.83667
R7-2 | RECEPTION | B | 14 | 700 | 482 | 482 | 0.68857
RTU-7 |  |  |  | 1000 |  | 733 | 0.733
NOTES: UNABLE TO REACH DAMPER FOR 7-2