## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
HP-1 | BAR | 5000 | 4869 | 4070 | 4869 | 930 | 0 | 18.6% | 0%
HP-2 | DINING | 2000 | 2183 | 1746 | 1927 | 254 | 256 | 12.7% | 11.73%
HP-3 | DINING | 3000 | 2864 | 2746 | 2567 | 254 | 297 | 8.467% | 10.37%
HP-4 | DINING/KITCHEN | 5000 | 4950 | 4382 | 4324 | 618 | 626 | 12.36% | 12.65%
HP-5 | DINING/KITCHEN | 3000 | 3191 | 2636 | 2817 | 364 | 374 | 12.13% | 11.72%
HP-6 | KITCHEN | 2000 | 2028 | 1744 | 2028 | 256 | 0 | 12.8% | 0%
HP-7 | DINING | 1600 | 1707 | 1388 | 1707 | 212 | 0 | 13.25% | 0%
HP-8 | DINING | 2400 | 2247 | 2118 | 2247 | 282 | 0 | 11.75% | 0%
HP-9 | DINING | 3000 | 3111 | 2746 | 3111 | 254 | 0 | 8.467% | 0%
ERTU-1 | OFFICES + BOH | 1400 | 1213 | 1125 | 915 | 275 | 298 | 19.64% | 24.57%
ERTU-3 | PRIVATE DINING | 1220 | 1277 | 875 | 1277 | 345 | 0 | 28.28% | 0%
MUA-1 | KITCHEN | [8 empty] | 4795 | 5029
KEF-1 | HOOD 1 | [10 empty] | 2364 | 2345
KEF-2 | HOOD 2 | [10 empty] | 3644 | 3408
KEF-3 | HOOD 3 | [10 empty] | 1125 | 1635
KEF-4 | HOOD 4 | [10 empty] | 675 | 723
EF-A1 | ORIGINAL RESTROOM | [12 empty] | 500 | 508
EF-1B | MEN/WOMEN RESTROOM | [12 empty] | 200 | 218
EF-2 | EMPLOYEE RESTROOM | [12 empty] | 100 | 92
TOTALS |  | 29620 | 29640 | 25576 | 27789 | 4044 | 1851 |  |  | 4795 | 5029 | 7808 | 8111 | 800 | 818
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 8839 | 6880 |  | FRONT |  | -0.138 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 8608 | 8929 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 231 | -2049 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.138 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0