## Sheet1
National TAB
Project: MD1440ZZ - Edward A. Garmatz (Baltimore, MD)
ASHRAE 62.1 Minimum Ventilation Rates
[10 empty] | Occupancy Category | CFM/Person | CFM/Sqft
Air Handling Units | [9 empty] | Office Building | 5 | 0.06
UNIT | Area Served | Space Type(s) Served | Sq Ft of Serviced Area | Occupant Population | SUPPLY CFM |  | HVAC RETURN |  | OUTDOOR Air CFM |  | Ashrae 62.1 calculated ventilation Rates (CFM) | Notes | Do not show - Formula reference only
[5 empty] | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | Courtrooms A & B | Courtrooms | 92813 | 898 | 72000 |  | 57600 |  | 14400 |  | 10058.78 |  | 10058.78
AHU-2 | Courtrooms C & D | Courtrooms | 70955 | 940 | 52000 |  | 41600 |  | 10400 |  | 8957.3 |  | 8957.3
AHU-3 | A Chambers | Office/Chambers | 36053 | 236 | 50000 |  | 40000 |  | 10000 |  | 3343.18 |  | 3343.18
AHU-4 | B Chambers | Office/Chambers | 26673 | 145 | 35000 |  | 28000 |  | 7000 |  | 2325.38 |  | 2325.38
AHU-5 | C Chambers | Office/Chambers | 18900 | 122 | 35000 |  | 28000 |  | 7000 |  | 1744 |  | 1744
AHU-6 | D Chambers | Office/Chambers | 17645 | 137 | 36000 |  | 28800 |  | 7200 |  | 1743.7 |  | 1743.7
AHU-7 | 6th Floor Cell block | Holding Cells |  | 17 | 9000 |  | 200 |  | 8800 |  | 85 |  | 85
AHU-8 | South Half Admin. Wing | Office | 46216 | 339 | 62000 |  | 43400 |  | 18600 |  | 4467.96 |  | 4467.96
AHU-9 | North Half Admin. Wing | Office | 37952 | 532 | 58000 |  | 40600 |  | 17400 |  | 4937.12 |  | 4937.12
AHU-10 | P level Janitorial Area | Janitorial | 2600 | 10 | 4400 |  | 1760 |  | 2640 |  | 206 |  | 206
AHU-11 | P level Mop room | Janitorial | 340 | 0 | 4600 |  | 0 |  | 4600 |  | 20.4 |  | 20.4
AHU-12 | P level Gun Range | Shooting Range | 1905 | 6 | 5000 |  | 0 |  | 5000 |  | 144.3 |  | 144.3
AHU-13 | Loading Dock Heat Only | Garage | 2805 | 0 | 4000 |  | 0 |  | 4000 |  | 168.3 |  | 168.3
AHU-14 | Café | Café | 3835 | 64 | 8000 |  | 6400 |  | 1600 |  | 550.1 |  | 550.1
AHU-15 | Garage Ceiling(Heat) | Garage |  | 0 | 11000 |  | 11000 |  |  |  | Occpuancy & Sqft Area Information Required | [3] | 0
AHU-16 | Backup Heat for Main Lobby | Lobby / Common Area |  | 0 |  |  | 0 |  |  |  | Occpuancy & Sqft Area Information Required | [3] | 0
AHU-1A | 3rd Floor Library | Library | 4800 |  |  |  | -3000 |  | 3000 |  | 288 |  | 288
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[1] | Design Outdoor Air CFM is less than ASHRAE Minimum Ventilation Rates based on occupancy and areas served information. Recommend adjusting and balancing to achieve ventilation airflow quantities.
0
[2] | Actual measured outdoor air CFM is less than ASHRAE minimum. Recommend testing, adjusting, and balancing to achieve optimum air flow rates. | [11 empty] | 0
0
[3] | Information not provided. Requesting information for the Occupancy Population and Sqft of serviced area. Population and sqft area must be provided to draw accurate conclusions and to compate ventilation rates to design and actual measurements. | [11 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Note on J27: ====== ID#AAAASv_6iwM (2021-12-03 14:54:55) Min OA from Spec of new AHU currently waiting for delivery -David Pule - 3PCC-C