## MD1440
REGION FILL OUT
Building name | MD1440ZZ - EDWARD A GARMATZ US CH, 101 W LOMBARD ST , BALTIMORE , MD
Current BAS | Alerton Compass 1.6.4
Current BAS contractor (technician) | Albireo Energy
O&M Name and Number | Raven Services Corp -
AHU number | AHU-1 | AHU-2 | AHU-3 | AHU-4 | AHU-5 | AHU-6 | AHU-7 | AHU-8 | AHU-9 | AHU-10 | AHU-11 | AHU-12 | AHU-13 | AHU-14 | AHU-15 | AHU-16 | AHU-1A
Areas / floors serviced | Courtrooms A & B | Courtrooms C & D | A Chambers | B Chambers | C Chambers | D Chambers | 6th Floor Cell block | South Half Admin. Wing | North Half Admin. Wing | P level Janitorial Area | P level Mop room | P level Gun Range | Loading Dock Heat Only | Café | Garage Ceiling(Heat) | Backup Heat for Main Lobby | 3rd Floor Library
Space type(s) served | Courtrooms | Courtrooms | Office/Chambers | Office/Chambers | Office/Chambers | Office/Chambers | Holding Cells | Office | Office | Janitorial | Janitorial | Shooting Range | Garage | Café | Garage | Lobby/Common Area | Library
Standard and New Extended Operating Hours
>Standard Start | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800 | 0800
>Standard End | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
>New Start | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500 | 0500
>New End | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Design OA Minimum (from existing drawings) | 14400 | 10400 | 10000 | 7000 | 7000 | 7200 | 8800 | 18600 | 17400 | 2640 | 4600 | 5000 | 4000 | 1600 | Garage Ceiling Only | Backup Heat Only | 3000
Design OA Maximum (from existing drawings) | 72000 | 52000 | 50000 | 35000 | 35000 | 36000 | 100% OA | 62000 | 58000 | 4400 | 100% OA | 100% OA | 100%OA | 8000 |  |  | 3000
Sq ft of serviced area | 92813 | 70955 | 36053 | 26673 | 18900 | 17645 |  | 46216 | 37952 | 2600 | 340 | 1905 | 2805 | 3835 |  |  | 4800
Occupant Population | 898 | 940 | 236 | 145 | 122 | 137 | 17 | 339 | 532 | 10 | 0 | 6 | 0 | 64 | 0 | 0
CONTRACTOR FILL OUT
Operating CFM
Confirm DCV Disabled (yes or no)
Confirm operating hours in the BAS
Measured Return CFM
Measured Maximum OA CFM
Measured Minimum OA CFM
OA Meas. Method (Direct PT or SA-RA PT)
>(If SA-RA) Measured Supply Air
>(If SA-RA) Measured Return Air
Pre-filter MERV Rating (or N/A)
Pre-filter size
Final Filter MERV Rating
Final Filter size
Comments / Corrective actions
Note on S15: ====== ID#AAAASv_6iwM (2021-12-03 14:54:55) Min OA from Spec of new AHU currently waiting for delivery -David Pule - 3PCC-C