## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 8963 | 7000 | 7227 | 1750 | 1736 | 20% | 19.37%
AC-2 | DRIVE THRU | 5250 | 5393 | 4000 | 4037 | 1250 | 1356 | 23.81% | 25.14%
AC-3 | DINNIND | 5250 | 5390 | 4100 | 4214 | 1150 | 1176 | 21.9% | 21.82%
AC-4 | BOH | 1875 | 1771 | 1375 | 1285 | 500 | 486 | 26.67% | 27.44%
EF-1 | HD1 | [10 empty] | 1913 | 1932
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1419
EF-3 | RESTROOM | [12 empty] | 375 | 380
TOTALS |  | 21125 | 21517 | 16475 | 16763 | 4650 | 4754 |  |  | 0 | 0 | 3315 | 3351 | 375 | 380
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4754 |  | FRONT |  | 0.0075 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3731 |  | SIDE |  | 0.0091 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 960 | 1023 |  | REAR |  | 0.0069 | [8 empty] | TRUE | FALSE | FALSE
[5 empty] | AVERAGE |  | 0.0078333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
TRUE
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390