## Report Sheet
STORE #: | 3976 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | SOUTH HAMILTON, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-06-02 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK |  |  | RTU-1 | KITCHEN | 500 | NA | 0 | 0 |  | NA | 1745 | NA | 1068 | 3 | NA | 209.5 | 3 | 9.4 | NA | 7 | 0 | 2.4515 | 0%
YORK | ZR120N18D2B5HAA1A1 | N1L7220555 | RTU-2 | DINING | 1000 | NA | 1000 | 0 |  | NA | 1726 | NA | 1034 | 3 | NA | 209.2 | 3 | 9.4 | NA | 7.3 | 0 | 2.5529 | 0%
CAPTIVE AIRE | A1-D.250-G10 | 4795740 | MUA-1 | HOOD 1 | 1950 | NA | 1700 | 1810 | No | NA | 1763 | NA | 894 | 2 | NA | 209.6 | 3 | 5.38 | NA | 2.66 | 0 | 0.932 | 0%
CAPTIVE AIRE | NCA24HPFA | 4795740 | EF-1 | HOOD 1 | 3200 | NA | 2450 | 2754 | No | NA | 1781 | NA | 781 | 2 | NA | 209.9 | 3 | 5.38 | NA | 3.01 | 0 | 1.0561 | 0%
| RR FAN RUNNING? | No | EF-2 | RESTROOM | 150 | 0 | 150 | 0
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | #VALUE! | 2700 | 1810 |  | FRONT DOOR |  | -0.0026 |  |  | INITIAL | 0 | 0
|  |  | TOTAL EXHAUST |  | 3350 | #VALUE! | 2600 | 2754 |  | BACK DOOR |  | -0.0012 |  |  | FINAL | 6.9924 | 4564
|  |  | NET AIRFLOW |  | 100 | #VALUE! | 100 | -944 |  | AVERAGE |  | -0.0019 |  |  | ∆ | -6.9924 | -4564
Issue List
Unit # | Description
Select from drop down list
RTU-1 | RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU-2 | RTU / OA Damper / Outside air damper is not functional and OA could not be set.
MUA | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
Initial file data corrupted/missaved. Returned to re-read after work had been completed, rendering original initia readings NA

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.