## AHU-8901
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8901 |  | Area: OA FOR AHU-8902 & AHU-8903
Unit Data |  |  | Test Data
Manufacurer | AIR ENTERPRISES |  |  | Design | Actual
Model Number | CUSTOM |  | SF CFM | 4000
Serial Number |  |  | SF RPM | 3186
Configuration | HORIZONTAL |  | RA CFM | 0
No. Pre Filters / Size | 4 / |  | OA CFM | 4000
No. Pre Filters / Size | 4 / |  | RL VOLTAGE | 460
No. Final Filters / Size |  |  | RL AMPERAGE
No. Final Filters / Size |  |  | Motor B.H.P. | 4.9
Motor Data |  |  | Performance Data
Motor MFG | BALDOR |  |  | Design | Actual
Frame | 213T |  | Suction S.P.
HP | 7.5 |  | Discharge S.P.
RPM | 3500 |  | Total SP | 5.35
Phase | 6 |  | CW Coil P.D.
Volts | 460 |  | HW Coil P.D.
Amps |  |  | Final Filters P.D.
Heat Wheel P.D.
Pre Filters P.D.
|  |  | Total ESP | 2.0

## AHU-8901 SGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8901 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8901-1 | OA AHU-8902 | DUCT | 12X30 | 2000 |  |  | 0
8901-2 | OA AHU-8903 | DUCT | 12X30 | 2000 |  |  | 0
|  |  |  | 4000 |  | 0 | 0

## AHU-8902
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 |  | Area: BUILDING 8
Unit Data |  |  | Test Data
Manufacurer | AIR ENTERPRISES |  |  | Design | Actual
Model Number | CUSTOM |  | SF CFM | 42000
Serial Number |  |  | SF RPM | 1123
Configuration | HORIZONTAL |  | RA CFM | 40000
No. Pre Filters / Size | 24 / |  | OA CFM | 2000
No. Pre Filters / Size | 24 / |  | RL VOLTAGE | 460
No. Final Filters / Size |  |  | RL AMPERAGE
No. Final Filters / Size |  |  | Motor B.H.P. | 68.1
Motor Data |  |  | Performance Data
Motor MFG | BALDOR |  |  | Design | Actual
Frame | 445T |  | Suction S.P.
HP | 100 |  | Discharge S.P.
RPM | 1200 |  | Total SP | 7.35
Phase | 3 |  | CW Coil P.D.
Volts | 460 |  | HW Coil P.D.
Amps |  |  | Final Filters P.D.
Heat Wheel P.D.
Pre Filters P.D.
|  |  | Total ESP | 4.0
NOTES: | SUPPLY & RETURN TWINNED WITH AHU-8903

## AHU-8903
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8903 |  | Area: BUILDING 8
Unit Data |  |  | Test Data
Manufacurer | AIR ENTERPRISES |  |  | Design | Actual
Model Number | CUSTOM |  | SF CFM | 42000
Serial Number |  |  | SF RPM | 1123
Configuration | HORIZONTAL |  | RA CFM | 40000
No. Pre Filters / Size | 24 / |  | OA CFM | 2000
No. Pre Filters / Size | 24 / |  | RL VOLTAGE | 460
No. Final Filters / Size |  |  | RL AMPERAGE
No. Final Filters / Size |  |  | Motor B.H.P. | 68.1
Motor Data |  |  | Performance Data
Motor MFG | BALDOR |  |  | Design | Actual
Frame | 445T |  | Suction S.P.
HP | 100 |  | Discharge S.P.
RPM | 1200 |  | Total SP | 7.35
Phase | 3 |  | CW Coil P.D.
Volts | 460 |  | HW Coil P.D.
Amps |  |  | Final Filters P.D.
Heat Wheel P.D.
Pre Filters P.D.
|  |  | Total ESP | 4.0
NOTES: | SUPPLY & RETURN TWINNED WITH AHU-8902

## AHU-8902 & 8903 RHC
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 & AHU-8903 RHC'S
Asset | Area Served | Size | Design Max CFM | Actual Max CFM
RHC-0801A | 08-0801 | 48 | 18340
RHC-0801B | 08-0801 | 48 | 18340
RHC-0801C | 08-0801 | 32 | 6800
RHC-0801D | 08-0801 | 26 | 3800
RHC-0801E | 08-0801 | 48 | 18340
RHC-0801F | 08-0801 | 48 | 18340
83960
Note on C7: NTAB: BILLINGSLEY ONLY

## RHC-0801A & B SGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: RHC-0801A & RHC-0801B SGRD'S
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
801A-1 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-2 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-3 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-4 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-5 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-6 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-7 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-8 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-9 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-10 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-11 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-12 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-13 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801A-14 | 08-0801 | K | 24X12 | 1310 |  |  | 0
RHC-0801A |  |  |  | 18340 |  | 0 | 0
801B-1 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-2 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-3 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-4 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-5 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-6 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-7 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-8 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-9 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-10 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-11 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-12 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-13 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801B-14 | 08-0801 | K | 24X12 | 1310 |  |  | 0
RHC-0801B |  |  |  | 18340 |  | 0 | 0

## RHC-0801C & D SGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: RHC-0801C & RHC-0801D SGRD'S
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
801C-1 | 08-0801 | K | 24X12 | 950 |  |  | 0
801C-2 | 08-0801 | K | 24X12 | 950 |  |  | 0
801C-3 | 08-0801 | K | 24X12 | 950 |  |  | 0
801C-4 | 08-0801 | K | 24X12 | 950 |  |  | 0
RHC-0801C |  |  |  | 3800 |  | 0 | 0
801D-1 | 08-0801 | K | 24X12 | 1130 |  |  | 0
801D-2 | 08-0801 | K | 24X12 | 1130 |  |  | 0
801D-3 | 08-0801 | K | 24X12 | 1140 |  |  | 0
801D-4 | 08-0801 | K | 24X12 | 1140 |  |  | 0
801D-5 | 08-0801 | K | 24X12 | 1130 |  |  | 0
801D-6 | 08-0801 | K | 24X12 | 1130 |  |  | 0
RHC-0801D |  |  |  | 6800 |  | 0 | 0

## RHC-0801E & F SGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: RHC-0801E & RHC-0801F SGRD'S
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
801E-1 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-2 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-3 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-4 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-5 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-6 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-7 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-8 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-9 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-10 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-11 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-12 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-13 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801E-14 | 08-0801 | K | 24X12 | 1310 |  |  | 0
RHC-0801E |  |  |  | 18340 |  | 0 | 0
801F-1 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-2 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-3 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-4 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-5 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-6 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-7 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-8 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-9 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-10 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-11 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-12 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-13 | 08-0801 | K | 24X12 | 1310 |  |  | 0
801F-14 | 08-0801 | K | 24X12 | 1310 |  |  | 0
RHC-0801F |  |  |  | 18340 |  | 0 | 0

## AHU-8902 & 8903 EGRD (1)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 & 8903 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R-1 | 08-0801 | K | 20X16 | 1300 |  |  | 0
|  |  |  | 1300 |  | 0 | 0
R-2 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-3 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-4 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-5 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-6 | 08-0801 | K | 18X12 | 1000 |  |  | 0
DUCT 1 |  |  |  | 5000 |  | 0 | 0
R-7 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-8 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-9 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-10 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-11 | 08-0801 | K | 16X10 | 360 |  |  | 0
DUCT 2 |  |  |  | 1800 |  | 0 | 0
R-12 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-13 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-14 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-15 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-16 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-17 | 08-0801 | K | 20X16 | 1300 |  |  | 0
DUCT 3 |  |  |  | 9700 |  | 0 | 0

## AHU-8902 & 8903 EGRD (2)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 & 8903 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R-18 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-19 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-20 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-21 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-22 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-23 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-24 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-25 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-26 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-27 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-28 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-29 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-30 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-31 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-32 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-33 | 08-0801 | K | 18X12 | 760 |  |  | 0
DUCT 4 |  |  |  | 12160 |  | 0 | 0

## AHU-8902 & 8903 EGRD (3)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 & 8903 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R-34 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-35 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-36 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-37 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-38 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-39 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-40 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-41 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-42 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-43 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-44 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-45 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-46 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-47 | 08-0801 | K | 18X12 | 760 |  |  | 0
DUCT 5 |  |  |  | 10640 |  | 0 | 0

## AHU-8902 & 8903 EGRD (4)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 & 8903 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R-48 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-49 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-50 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-51 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-52 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-53 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-54 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-55 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-56 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-57 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-58 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-59 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-60 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-61 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-62 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-63 | 08-0801 | K | 18X12 | 760 |  |  | 0
DUCT 6 |  |  |  | 12160 |  | 0 | 0

## AHU-8902 & 8903 EGRD (5)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 & 8903 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R-64 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-65 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-66 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-67 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-68 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-69 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-70 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-71 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-72 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-73 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-74 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-75 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-76 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-77 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-78 | 08-0801 | K | 18X12 | 760 |  |  | 0
R-79 | 08-0801 | K | 18X12 | 760 |  |  | 0
DUCT 7 |  |  |  | 12160 |  | 0 | 0

## AHU-8902 & 8903 EGRD (6)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8902 & 8903 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R-80 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-81 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-82 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-83 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-84 | 08-0801 | K | 30X14 | 1680 |  |  | 0
R-85 | 08-0801 | K | 20X16 | 1300 |  |  | 0
DUCT 8 |  |  |  | 9700 |  | 0 | 0
R-86 | 08-0801 | K | 20X16 | 1300 |  |  | 0
|  |  |  | 1300 |  | 0 | 0
R-87 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-88 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-89 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-90 | 08-0801 | K | 16X10 | 360 |  |  | 0
R-91 | 08-0801 | K | 16X10 | 360 |  |  | 0
DUCT 9 |  |  |  | 1800 |  | 0 | 0
R-92 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-93 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-94 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-95 | 08-0801 | K | 18X12 | 1000 |  |  | 0
R-96 | 08-0801 | K | 18X12 | 1000 |  |  | 0
DUCT 10 |  |  |  | 5000 |  | 0 | 0

## AHU-8951
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8951 |  | Area: SAMPLING SUITE 10-1006
Unit Data |  |  | Test Data
Manufacurer | AIR ENTERPRISES |  |  | Design | Actual
Model Number | CUSTOM |  | SF CFM | 4500
Serial Number |  |  | SF RPM | 3446
Configuration | HORIZONTAL |  | RA CFM | 2500
No. Pre Filters / Size |  |  | OA CFM | 2000
No. Pre Filters / Size |  |  | RL VOLTAGE | 460
No. Final Filters / Size |  |  | RL AMPERAGE
No. Final Filters / Size |  |  | Motor B.H.P. | 9.02
Motor Data |  |  | Performance Data
Motor MFG | BALDOR |  |  | Design | Actual
Frame | 215T |  | Suction S.P.
HP | 10 |  | Discharge S.P.
RPM | 2600 |  | Total SP | 8.61
Phase | 3 |  | CW Coil P.D.
Volts | 460 |  | HW Coil P.D.
Amps |  |  | Final Filters P.D.
Heat Wheel P.D.
Pre Filters P.D.
|  |  | Total ESP | 4.00

## AHU-8951 Air Valves
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8951 AIR VALVES
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Ak (max)
LVS-1006 | 10-1006 | SUPPLY | 14 | 2400 |  | 2400
LVS-1009 | 10-1009 | SUPPLY | 12 | 580 |  | 580
LVS-1010 | 10-1010 | SUPPLY | 8 | 180 |  | 180
LVS-1011 | 10-1011 | SUPPLY | 8 | 170 |  | 170
LVS-1012 | 10-1012 | SUPPLY | 12 | 500 |  | 500
LVS-1013 | 10-1013 | SUPPLY | 8 | 190 |  | 190
LVS-1014 | 10-1014 | SUPPLY | 8 | 230 |  | 230
SUPPLY |  |  |  | 4250 | 0 | 4250 | 0
LVR-1006 | 10-1006 | RETURN | 14 | 1150 |  | 680
RETURN |  |  |  | 1150 | 0 | 680 | 0
LVE-1006 | 10-1006 | EXHAUST | 12 | 1200 |  | 600
EXHAUST |  |  |  | 1200 | 0 | 600 | 0

## AHU-8951 Air Valves SGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8951 AIR VALVE SGRD
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1006-1 | 10-1006 | F | 12 | 480 |  |  | 0
1006-2 | 10-1006 | F | 12 | 480 |  |  | 0
1006-3 | 10-1006 | F | 12 | 480 |  |  | 0
1006-4 | 10-1006 | F | 12 | 480 |  |  | 0
1006-5 | 10-1006 | F | 12 | 480 |  |  | 0
LVS-1006 |  |  |  | 2400 |  | 0 | 0
1009-1 | 10-1009 | F | 12 | 290 |  |  | 0
1009-2 | 10-1009 | F | 12 | 290 |  |  | 0
LVS-1009 |  |  |  | 580 |  | 0 | 0
1010-1 | 10-1010 | E | 10 | 180 |  |  | 0
LVS-1010 |  |  |  | 180 |  | 0 | 0
1011-1 | 10-1011 | E | 10 | 170 |  |  | 0
LVS-1011 |  |  |  | 170 |  | 0 | 0
1012-1 | 10-1012 | F | 12 | 250 |  |  | 0
1012-2 | 10-1012 | F | 12 | 250 |  |  | 0
LVS-1012 |  |  |  | 500 |  | 0 | 0
1013-1 | 10-1013 | E | 10 | 190 |  |  | 0
LVS-1013 |  |  |  | 190 |  | 0 | 0
1014-1 | 10-1014 | E | 10 | 230 |  |  | 0
LVS-1014 |  |  |  | 230 |  | 0 | 0

## AHU-8951 Air Valves EGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8951 AIR VALVE EXHAUST & RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
STOR CABINET | 10-1006 | NA | 16 | 1200 |  |  | 0
LVE-1006 |  |  |  | 1200 |  | 0 | 0
R1006-1 | 10-1006 | CLOTH | 20X6 |  |  |  | #DIV/0!
R1006-2 | 10-1006 | CLOTH | 20X6 |  |  |  | #DIV/0!
R1006-3 | 10-1006 | CLOTH | 20X6 |  |  |  | #DIV/0!
R1006-4 | 10-1006 | CLOTH | 20X6 |  |  |  | #DIV/0!
R1006-5 | 10-1006 | CLOTH | 20X6 |  |  |  | #DIV/0!
LVR-1006 |  |  |  | 0 |  | 0 | #DIV/0!

## AHU-8951 EGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8951 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R8951-1 | 10-1010 | CLOTH | 10X6 |  |  |  | #DIV/0!
R8951-2 | 10-1009 | CLOTH | 20X6 |  |  |  | #DIV/0!
R8951-3 | 10-1011 | CLOTH | 8 |  |  |  | #DIV/0!
R8951-4 | 10-1012 | CLOTH | 20X6 |  |  |  | #DIV/0!
R8951-5 | 10-1013 | CLOTH | 10X6 |  |  |  | #DIV/0!
R8951-6 | 10-1014 | CLOTH | 12X6 |  |  |  | #DIV/0!
|  |  |  | 0 |  | 0 | #DIV/0!

## AHU-8952
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8951 |  | Area: LOADING DOCK 10-1000
Unit Data |  |  | Test Data
Manufacurer | AIR ENTERPRISES |  |  | Design | Actual
Model Number | CUSTOM |  | SF CFM | 51000
Serial Number |  |  | SF RPM | 1137
Configuration | HORIZONTAL |  | RA CFM | 43000
No. Pre Filters / Size |  |  | OA CFM | 8000
No. Pre Filters / Size |  |  | RL VOLTAGE | 460
No. Final Filters / Size |  |  | RL AMPERAGE
No. Final Filters / Size |  |  | Motor B.H.P. | 90.4
Motor Data |  |  | Performance Data
Motor MFG | BALDOR |  |  | Design | Actual
Frame | 444T |  | Suction S.P.
HP | 100 |  | Discharge S.P.
RPM | 1200 |  | Total SP | 8.16
Phase | 3 |  | CW Coil P.D.
Volts | 460 |  | HW Coil P.D.
Amps |  |  | Final Filters P.D.
Heat Wheel P.D.
Pre Filters P.D.
|  |  | Total ESP | 3.00

## AHU-8951 & 8952 RHC
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8951 & AHU-8952 RHC'S
Asset | Area Served |  | Size | Design Max CFM | Actual Max CFM
RHC-8951 (1) | 10-1006 |  | 30X18 | 4250
AHU-8951
RHC-1000A | 10-1000 | DUCT 1 | 46X30 | 13980
RHC-1000B | 10-1000 | DUCT 2 | 46X30 | 14800
RHC-2009 | 10-2003 | DUCT 3 | 12 | 500
RHC-2007 | 10-2006, 10-2007 | DUCT 4 | 14 | 690
RHC-1017 | 10-1017 | DUCT 5 | 10 | 320
RHC-1018 | 10-1018 | DUCT 6 | 10 | 270
RHC-1001 | 10-1001, 10-1003A | DUCT 7 | 12 | 550
RHC-1003 | 10-1003, 10-1003B | DUCT 8 | 14 | 800
RHC-1005 | 10-1005 | DUCT 9 | 18 | 1550
RHC-1021 | 10-1021 | DUCT 10 | 8 | 200
RHC-2015 | 10-2015 | DUCT 11 | 8 | 130
RHC-1016A | 10-1000 | DUCT 12 | 36X26 | 7475
RHC-1016B | 10-1000 | DUCT 13 | 36X26 | 8450
AHU-8952
NOTES: | (1) ALL LVS SUPPLY AIR VALVES

## AHU-8952 SGRD (1)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8952 DUCT 1 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8952-1 | 10-1000 | A | 16 | 830 |  |  | 0
8952-2 | 10-1000 | A | 16 | 830 |  |  | 0
8952-3 | 10-1000 | A | 16 | 820 |  |  | 0
8952-4 | 10-1000 | A | 16 | 820 |  |  | 0
8952-5 | 10-1000 | A | 16 | 820 |  |  | 0
8952-6 | 10-1000 | A | 16 | 830 |  |  | 0
8952-7 | 10-1000 | A | 16 | 820 |  |  | 0
8952-8 | 10-1000 | A | 16 | 820 |  |  | 0
8952-9 | 10-1000 | A | 16 | 820 |  |  | 0
8952-10 | 10-1000 | A | 16 | 825 |  |  | 0
8952-11 | 10-1000 | A | 16 | 820 |  |  | 0
8952-12 | 10-1000 | A | 16 | 820 |  |  | 0
8952-13 | 10-1000 | A | 16 | 820 |  |  | 0
8952-14 | 10-1000 | A | 16 | 825 |  |  | 0
8952-15 | 10-1000 | A | 16 | 820 |  |  | 0
8952-16 | 10-1000 | A | 16 | 820 |  |  | 0
8952-17 | 10-1000 | A | 16 | 820 |  |  | 0
DUCT 1 |  |  |  | 13980 |  | 0 | 0

## AHU-8952 SGRD (2)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8952 DUCT 2 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8952-18 | 10-1000 | A | 16 | 830 |  |  | 0
8952-19 | 10-1000 | A | 16 | 820 |  |  | 0
8952-20 | 10-1000 | A | 16 | 820 |  |  | 0
8952-21 | 10-1000 | A | 16 | 820 |  |  | 0
8952-22 | 10-1000 | A | 16 | 830 |  |  | 0
8952-23 | 10-1000 | A | 16 | 820 |  |  | 0
8952-24 | 10-1000 | A | 16 | 820 |  |  | 0
8952-25 | 10-1000 | A | 16 | 820 |  |  | 0
8952-26 | 10-1000 | A | 16 | 830 |  |  | 0
8952-27 | 10-1000 | A | 16 | 820 |  |  | 0
8952-28 | 10-1008 | C | 8 | 100 |  |  | 0
8952-29 | 10-1000 | A | 16 | 720 |  |  | 0
8952-30 | 10-1000 | A | 16 | 830 |  |  | 0
8952-31 | 10-1000 | A | 16 | 820 |  |  | 0
8952-32 | 10-1000 | A | 16 | 820 |  |  | 0
8952-33 | 10-1000 | A | 16 | 820 |  |  | 0
8952-34 | 10-1000 | A | 16 | 820 |  |  | 0
8952-35 | 10-1000 | A | 16 | 820 |  |  | 0
8952-36 | 10-1000 | A | 16 | 820 |  |  | 0
DUCT 2 |  |  |  | 14800 |  | 0 | 0

## AHU-8952 SGRD (3)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8952 DUCTS 3-7 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8952-37 | 10-2003 | C | 8 | 100 |  |  | 0
8952-38 | 10-2003 | C | 8 | 100 |  |  | 0
8952-39 | 10-2003 | C | 8 | 100 |  |  | 0
8952-40 | 10-2009 | C | 8 | 100 |  |  | 0
8952-41 | 10-2009 | C | 8 | 100 |  |  | 0
RHC-2009 DUCT 3 |  |  |  | 500 |  | 0 | 0
8952-42 | 10-2007 | C | 8 | 115 |  |  | 0
8952-43 | 10-2007 | C | 8 | 115 |  |  | 0
8952-44 | 10-2007 | C | 8 | 115 |  |  | 0
8952-45 | 10-2006 | C | 8 | 115 |  |  | 0
8952-46 | 10-2006 | C | 8 | 115 |  |  | 0
8952-47 | 10-2006 | C | 8 | 115 |  |  | 0
RHC-2007 DUCT 4 |  |  |  | 690 |  | 0 | 0
8952-48 | 10-1017 | C | 10 | 320 |  |  | 0
RHC-1017 DUCT 5 |  |  |  | 320 |  | 0 | 0
8952-49 | 10-1018 | C | 10 | 270 |  |  | 0
RHC-1018 DUCT 6 |  |  |  | 270 |  | 0 | 0
8952-50 | 10-1001 | C | 8 | 100 |  |  | 0
8952-51 | 10-1003A | C | 8 | 150 |  |  | 0
8952-52 | 10-1020 | M | 6 | 50 |  |  | 0
8952-53 | 10-1001 | C | 8 | 125 |  |  | 0
8952-54 | 10-1001 | C | 8 | 125 |  |  | 0
RHC-1001 DUCT 7 |  |  |  | 550 |  | 0 | 0

## AHU-8952 SGRD (4)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8952 DUCTS 8-11 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8952-55 | 10-1003 | C | 8 | 200 |  |  | 0
8952-56 | 10-1003 | C | 8 | 200 |  |  | 0
8952-57 | 10-1003 | C | 8 | 200 |  |  | 0
8952-58 | 10-1003B | C | 8 | 200 |  |  | 0
RHC-1003 DUCT 8 |  |  |  | 800 |  | 0 | 0
8952-59 | 10-1005 | C | 12 | 385 |  |  | 0
8952-60 | 10-1005 | C | 12 | 390 |  |  | 0
8952-61 | 10-1005 | C | 12 | 390 |  |  | 0
8952-62 | 10-1005 | C | 12 | 385 |  |  | 0
RHC-1005 DUCT 9 |  |  |  | 1550 |  | 0 | 0
8952-63 | 10-1021 | M | 8 | 200 |  |  | 0
RHC-1021 DUCT 10 |  |  |  | 200 |  | 0 | 0
8952-64 | 10-2015 | C | 8 | 130 |  |  | 0
RHC-2015 DUCT 11 |  |  |  | 130 |  | 0 | 0

## AHU-8952 SGRD (5)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8952 DUCT 12 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8952-65 | PALLET WASH | B | 10 | 325 |  |  | 0
8952-66 | PALLET WASH | B | 10 | 325 |  |  | 0
8952-67 | 10-1000 | B | 10 | 325 |  |  | 0
8952-68 | 10-1000 | B | 10 | 325 |  |  | 0
8952-69 | 10-1000 | B | 10 | 325 |  |  | 0
8952-70 | 10-1000 | B | 10 | 325 |  |  | 0
8952-71 | 10-1000 | B | 10 | 325 |  |  | 0
8952-72 | 10-1000 | B | 10 | 325 |  |  | 0
8952-73 | 10-1000 | B | 10 | 325 |  |  | 0
8952-74 | 10-1000 | B | 10 | 325 |  |  | 0
8952-75 | 10-1000 | B | 10 | 325 |  |  | 0
8952-76 | 10-1000 | B | 10 | 325 |  |  | 0
8952-77 | 10-1000 | B | 10 | 325 |  |  | 0
8952-78 | 10-1000 | B | 10 | 325 |  |  | 0
8952-79 | 10-1000 | B | 10 | 325 |  |  | 0
8952-80 | 10-1000 | B | 10 | 325 |  |  | 0
8952-81 | 10-1000 | B | 10 | 325 |  |  | 0
8952-82 | 10-1000 | B | 10 | 325 |  |  | 0
8952-83 | 10-1000 | B | 10 | 325 |  |  | 0
8952-84 | 10-1000 | B | 10 | 325 |  |  | 0
8952-85 | 10-1000 | B | 10 | 325 |  |  | 0
8952-86 | 10-1000 | B | 10 | 325 |  |  | 0
8952-87 | 10-1000 | B | 10 | 325 |  |  | 0
RHC-1016A DUCT 12 |  |  |  | 7475 |  | 0 | 0

## AHU-8952 SGRD (6)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8952 DUCT 13 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8952-88 | 10-1000 | B | 10 | 325 |  |  | 0
8952-89 | 10-1000 | B | 10 | 325 |  |  | 0
8952-90 | 10-1000 | B | 10 | 325 |  |  | 0
8952-91 | 10-1000 | B | 10 | 325 |  |  | 0
8952-92 | 10-1000 | B | 10 | 325 |  |  | 0
8952-93 | 10-1000 | B | 10 | 325 |  |  | 0
8952-94 | 10-1000 | B | 10 | 325 |  |  | 0
8952-95 | 10-1000 | B | 10 | 325 |  |  | 0
8952-96 | 10-1000 | B | 10 | 325 |  |  | 0
8952-97 | 10-1000 | B | 10 | 325 |  |  | 0
8952-98 | 10-1000 | B | 10 | 325 |  |  | 0
8952-99 | 10-1000 | B | 10 | 325 |  |  | 0
8952-100 | 10-1000 | B | 10 | 325 |  |  | 0
8952-101 | 10-1000 | B | 10 | 325 |  |  | 0
8952-102 | 10-1000 | B | 10 | 325 |  |  | 0
8952-103 | 10-1000 | B | 10 | 325 |  |  | 0
8952-104 | 10-1000 | B | 10 | 325 |  |  | 0
8952-105 | 10-1000 | B | 10 | 325 |  |  | 0
8952-106 | 10-1000 | B | 10 | 325 |  |  | 0
8952-107 | 10-1000 | B | 10 | 325 |  |  | 0
8952-108 | 10-1000 | B | 10 | 325 |  |  | 0
8952-109 | 10-1000 | B | 10 | 325 |  |  | 0
8952-110 | 10-1000 | B | 10 | 325 |  |  | 0
8952-111 | 10-1000 | B | 10 | 325 |  |  | 0
8952-112 | 10-1000 | B | 10 | 325 |  |  | 0
8952-113 | 10-1000 | B | 10 | 325 |  |  | 0
DUCT 13 |  |  |  | 8450 |  | 0 | 0

## AHU-8952 EGRD
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: AHU-8952 RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
R8952-1 | 10-2003 (1) | CLOTH | 14 | 500 |  |  | 0
R8952-2 | 10-2015 | D | 8 | 130 |  |  | 0
R8952-3 | 10-1021 | L | 8 |  |  |  | #DIV/0!
R8952-4 | 10-1000 (2) | CLOTH | 24X42 | 4875 |  |  | 0
R8952-5 | 10-1000 (3) | CLOTH | 24X42 | 11050 |  |  | 0
R8952-6 | 10-1000 (4) | CLOTH | 54X50 | 28780 |  |  | 0
R8952-7 | 10-1005 | D | 12 | 780 |  |  | 0
R8952-8 | 10-1005 | D | 12 | 770 |  |  | 0
R8952-9 | 10-1017 | D | 12 | 320 |  |  | 0
R8952-10 | 10-1018 | D | 8 | 270 |  |  | 0
|  |  |  | 46845 |  | 0 | 0
NOTES: | (1) TOTAL OF SUPPLY DIFFUSERS 37-41
(2) TOTAL OF SUPPLY DIFFUSERS 99-113
(3) TOTAL OF SUPPLY DIFFUSERS 66-98
(4) TOTAL OF SUPPLY DIFFUSERS 1-36

## FCU-2000
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU-2000 |  | Area: 10-2000
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0301 |  |  |  | SA CFM | 550
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 0
[5 empty] | RA CFM | 550
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2000-1 | 10-2000 | H | 12X8 | 275 |  |  | 0
2000-2 | 10-2000 | H | 12X8 | 275 |  |  | 0
|  |  |  | 550 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-2004
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU-2004 |  | Area: 10-2004
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0061 |  |  |  | SA CFM | 3120
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 0
[5 empty] | RA CFM | 3120
Motor Data |  |  |  |  | RL Voltage | 115
Motor MFG |  |  |  |  | RL Amperage
Horsepower | 0.33 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.5
Voltage (rated) | 115 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2004-1 | 10-2004 | H | 18X12 | 780 |  |  | 0
2004-2 | 10-2004 | H | 18X12 | 780 |  |  | 0
2004-3 | 10-2004 | H | 18X12 | 780 |  |  | 0
2004-4 | 10-2004 | H | 18X12 | 780 |  |  | 0
|  |  |  | 3120 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-2005
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU2005 |  | Area:
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0101 |  |  |  | SA CFM | 850
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 0
[5 empty] | RA CFM | 850
Motor Data |  |  |  |  | RL Voltage | 115
Motor MFG |  |  |  |  | RL Amperage | 6.4
Horsepower | 0.5 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.5
Voltage (rated) | 115 |  |  |  | Brake HP
Amperage (rated) | 6.4
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2005-1 | 10-2005 | H | 12X8 | 425 |  |  | 0
2005-2 | 10-2005 | H | 12X8 | 425 |  |  | 0
SUPPLY |  |  |  | 850 |  | 0 | 0
R2005-1 | 10-2008 | CLOTH | 8X8 | 150 |  |  | 0
R2005-2 | 10-2005 | CLOTH | 14X12 | 700 |  |  | 0
RETURN |  |  |  | 850 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-2008A
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU2008A |  | Area: 10-2008
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0401 |  |  |  | SA CFM | 3340
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 340
[5 empty] | RA CFM | 3000
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage | 8.4
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1.5
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated) | 8.4
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2008A-1 | 10-2008 | G | 36X12 | 1670 |  |  | 0
2008A-2 | 10-2008 | G | 36X12 | 1670 |  |  | 0
|  |  |  | 3340 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-2008B
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU2008-B |  | Area: 10-2008
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0401 |  |  |  | SA CFM | 3340
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 340
[5 empty] | RA CFM | 3000
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage | 8.4
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1.5
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated) | 8.4
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2008B-1 | 10-2008 | G | 36X12 | 1670 |  |  | 0
2000B-2 | 10-2008 | G | 36X12 | 1670 |  |  | 0
|  |  |  | 3340 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-2008C
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU-2008C |  | Area: 10-2008
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0401 |  |  |  | SA CFM | 3360
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 340
[5 empty] | RA CFM | 3020
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage | 8.4
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1.5
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated) | 8.4
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2008C-1 | 10-2008 | G | 36X12 | 1120 |  |  | 0
2008C-2 | 10-2008 | G | 36X12 | 1120 |  |  | 0
2008C-3 | 10-2008 | G | 36X12 | 1120 |  |  | 0
|  |  |  | 3360 |  |  | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-2008D
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU-2008D |  | Area: 10-2008
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0401 |  |  |  | SA CFM | 3360
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 340
[5 empty] | RA CFM | 3020
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage | 8.4
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1.5
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated) | 8.4
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2008D-1 | 10-2008 | G | 36X12 | 1120 |  |  | 0
2008D-2 | 10-2001 | H | 18X10 | 560 |  |  | 0
2008D-3 | 10-2001 | H | 18X10 | 560 |  |  | 0
2008D-4 | 10-2008 | G | 36X12 | 1120 |  |  | 0
|  |  |  | 3360 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-2008E
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU-2008E |  | Area: 10-2008
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0401 |  |  |  | SA CFM | 3360
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 340
[5 empty] | RA CFM | 3020
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage | 8.4
Horsepower | 3 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1.5
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated) | 8.4
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2008E-1 | 10-2008 | G | 36X12 | 1120 |  |  | 0
2008E-2 | 10-2008 | G | 36X12 | 1120 |  |  | 0
2008E-3 | 10-2008 | G | 36X12 | 1120 |  |  | 0
|  |  |  | 3360 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU-ST01
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FCU-ST01 |  | Area: STAIRS
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0301 |  |  |  | SA CFM | 1830
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 0
[5 empty] | RA CFM | 1830
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage | 4.8
Horsepower | 1.5 |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 1
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated) | 4.8
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
ST01-1 | STAIRS | C | 14 | 610 |  |  | 0
ST01-2 | STAIRS | C | 14 | 610 |  |  | 0
ST01-3 | STAIRS | C | 14 | 610 |  |  | 0
|  |  |  | 1830 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FFU-1023
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FFU-1023 |  | Area: 10-1023
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | BCHD0101 |  |  |  | SA CFM | 1000
Serial Num |  |  |  |  | Fan RPM | 2002
[5 empty] | OA CFM | 0
Motor Data |  |  |  |  | RA CFM | 1000
Motor MFG |  |  |  |  | RL Voltage | 115
Horsepower |  |  |  |  | RL Amperage
Motor Rpm |  |  |  |  | Suction ESP
Phase | 1 |  |  |  | Discharge ESP
Voltage (rated) | 115 |  |  |  | Total ESP | 2
Amperage (rated) |  |  |  |  | Brake HP | 0.97
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1023-1 | 10-1023 | J | 4 | 48 |  |  | 0
1023-2 | 10-1023 | J | 4 | 48 |  |  | 0
1023-3 | 10-1023 | J | 4 | 48 |  |  | 0
1023-4 | 10-1023 | J | 4 | 48 |  |  | 0
1023-5 | 10-1023 | J | 4 | 48 |  |  | 0
1023-6 | 10-1023 | J | 4 | 48 |  |  | 0
1023-7 | 10-1023 | J | 4 | 48 |  |  | 0
1023-8 | 10-1023 | J | 4 | 48 |  |  | 0
1023-9 | 10-1023 | J | 4 | 48 |  |  | 0
1023-10 | 10-1023 | J | 4 | 48 |  |  | 0
1023-11 | 10-1023 | J | 4 | 48 |  |  | 0
1023-12 | 10-1023 | J | 4 | 48 |  |  | 0
1023-13 | 10-1023 | J | 4 | 48 |  |  | 0
1023-14 | 10-1023 | J | 4 | 48 |  |  | 0
1023-15 | 10-1023 | J | 4 | 48 |  |  | 0
SUPPLY |  |  |  | 720 |  | 0 | 0
R1023-1 | 10-1023 |  | 16X6 | 350 |  |  | 0
R1023-2 | 10-1023 |  | 16X6 | 350 |  |  | 0
RETURN |  |  |  | 700 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FAN-2000EX
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FAN-2000EX |  | Area:
Unit Data |  |  | Test Data
MFG | TWIN CITY FAN |  |  | Design | Actual
Model Num | DSI 135ANE |  | CFM | 600
Serial Num |  |  | Fan RPM | 1229
Type | INLINE |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 1
Frame
Horsepower | 0.75
Motor Rpm | 1750
Phase | 1
Voltage (rated) | 115
Amperage (rated)
Service Factor
-

## FAN-8951EX
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FAN-8951EX |  | Area: SAMPLING SUITE
Unit Data |  |  | Test Data
MFG | AEROVENT |  |  | Design | Actual
Model Num | 135/CB-SW |  | CFM | 1120
Serial Num |  |  | Fan RPM
Type | CRE UPBLAST |  | RL Voltage | 460
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 1
Frame | 143T
Horsepower | 1
Motor Rpm | 1800
Phase | 3
Voltage (rated) | 460
Amperage (rated)
Service Factor
-

## FAN-8952AEX
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FAN-8952AEX |  | Area: PALLET WASHER
Unit Data |  |  | Test Data
MFG | AEROVENT |  |  | Design | Actual
Model Num | 165/CB-SW |  | CFM | 2800
Serial Num |  |  | Fan RPM
Type | CRE UPBLAST |  | RL Voltage | 460
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 2
Frame | 145T
Horsepower | 2
Motor Rpm | 1800
Phase | 3
Voltage (rated) | 460
Amperage (rated)
Service Factor
-

## FAN-8952BEX
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: FAN-8952BEX |  |  | Area: UPS ROOM 10-2000
Unit Data |  |  |  |  | Test Data
MFG |  | AEROVENT |  |  |  | Design | Actual
Model Num |  | 135/CB/SW |  |  | CFM | 1000
Serial Num |  |  |  |  | Fan RPM
Type |  | CRE UPBLAST |  |  | RL Voltage | 460
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 2
Frame |  | 143T
Horsepower |  | 1
Motor Rpm |  | 1800
Phase |  | 3
Voltage (rated) |  | 460
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
8952B-1 | 10-2006 | D | 12 | 450 |  |  | 0
8952B-2 | RESTROOM | L | 6 | 100 |  |  | 0
8952B-3 | 10-2007 | D | 12 | 450 |  |  | 0
|  |  |  | 1000 |  | 0 | 0
-

## P-8901PH Pump
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: P-8901PH |  | Service: AHU-8901 HHW
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG |  |  | Pump Off Pressure (psi)
Model Num |  |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service |  |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head |  |  | Discharge Pressure (ft)
Impellar Diameter |  |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 12
Motor Data |  |  | Final GPM | 13
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 115
Horsepower |  |  | RL Amperage
Motor RPM |  |  | BHP
Phase | 1
Voltage | 115
Amperage
Service Factor
Efficiency
Power Factor

## P-8951PH Pump
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: P-8951PH |  | Service: AHU-8951 HHW
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG |  |  | Pump Off Pressure (psi)
Model Num |  |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service |  |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head |  |  | Discharge Pressure (ft)
Impellar Diameter |  |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 12
Motor Data |  |  | Final GPM | 13
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 115
Horsepower |  |  | RL Amperage
Motor RPM |  |  | BHP
Phase | 1
Voltage | 115
Amperage
Service Factor
Efficiency
Power Factor

## P-8952PH Pump
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: P-8952PH |  | Service: AHU-8952 HHW
Unit Data |  |  | Test Data
|  |  |  | Design | Actual
MFG |  |  | Pump Off Pressure (psi)
Model Num |  |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service |  |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head |  |  | Discharge Pressure (ft)
Impellar Diameter |  |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 12
Motor Data |  |  | Final GPM | 13
Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 115
Horsepower |  |  | RL Amperage
Motor RPM |  |  | BHP
Phase | 1
Voltage | 115
Amperage
Service Factor
Efficiency
Power Factor

## P-8660E
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: P-8660E |  | Location: 10-2008
Unit Data |  |  | Test Data
|  |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1532 3EB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service | GLYCOL SYSTEM |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head |  |  | Discharge Pressure (ft)
Impellar Diameter | 11 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 100
Motor Data |  |  | Final GPM | 364
Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 20 |  | RL Amperage | 27.0
Motor RPM | 1800 |  | BHP | 13.5
Phase | 3
Voltage | 460
Amperage | 27.0
Service Factor
Efficiency
Power Factor

## P-8660F
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: P-8660F |  | Location: 10-2008
Unit Data |  |  | Test Data
|  |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1532 3EB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service | GLYCOL SYSTEM |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head |  |  | Discharge Pressure (ft)
Impellar Diameter | 11 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 100
Motor Data |  |  | Final GPM | 364
Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 20 |  | RL Amperage | 27.0
Motor RPM | 1800 |  | BHP | 13.5
Phase | 3
Voltage | 460
Amperage | 27.0
Service Factor
Efficiency
Power Factor

## P-8660G
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: P-8660G |  | Location: 10-2008
Unit Data |  |  | Test Data
|  |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1532 3EB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service | GLYCOL SYSTEM |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head |  |  | Discharge Pressure (ft)
Impellar Diameter | 11 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 100
Motor Data |  |  | Final GPM | 364
Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 20 |  | RL Amperage | 27.0
Motor RPM | 1800 |  | BHP | 13.5
Phase | 3
Voltage | 460
Amperage | 27.0
Service Factor
Efficiency
Power Factor

## Glycol Chiller AC (1)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: CHLR-8660A (AIR COOLED) |  |  | Asset: CHLR-8660B (AIR COOLED)
UNIT DATA |  |  | UNIT DATA
Unit Description |  |  | Unit Description
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | TPACVMV0600D4-MM |  | Model Number | TPACVMV0600D4-MM
Serial Number |  |  | Serial Number
EVAPORATOR DATA | Design | Actual | EVAPORATOR DATA | Design | Actual
Flow GPM | 450.8 |  | Flow GPM | 450.8
Pressure Drop | 14.3 |  | Pressure Drop | 14.3
Asset: CHLR-8660C (AIR COOLED) |  |  | Asset: CHLR-8660D (AIR COOLED)
UNIT DATA |  |  | UNIT DATA
Unit Description |  |  | Unit Description
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | TPACVMV0600D4-MM |  | Model Number | TPACVMV0600D4-MM
Serial Number |  |  | Serial Number
EVAPORATOR DATA | Design | Actual | EVAPORATOR DATA | Design | Actual
Flow GPM | 450.8 |  | Flow GPM | 450.8
Pressure Drop | 14.3 |  | Pressure Drop | 14.3

## Glycol Chiller AC (2)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: CHLR-8660E (AIR COOLED) |  |  | Asset: CHLR-8660F (AIR COOLED)
UNIT DATA |  |  | UNIT DATA
Unit Description |  |  | Unit Description
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | TPACVMV0600D4-MM |  | Model Number | TPACVMV0600D4-MM
Serial Number |  |  | Serial Number
EVAPORATOR DATA | Design | Actual | EVAPORATOR DATA | Design | Actual
Flow GPM | 450.8 |  | Flow GPM | 450.8
Pressure Drop | 14.3 |  | Pressure Drop | 14.3
Asset: CHLR-8660G (AIR COOLED) |  |  | Asset: CHLR-8660H (AIR COOLED)
UNIT DATA |  |  | UNIT DATA
Unit Description |  |  | Unit Description
Manufacturer | TRANE |  | Manufacturer | TRANE
Model Number | TPACVMV0600D4-MM |  | Model Number
Serial Number |  |  | Serial Number
EVAPORATOR DATA | Design | Actual | EVAPORATOR DATA | Design | Actual
Flow GPM | 450.8 |  | Flow GPM | 450.8
Pressure Drop | 14.3 |  | Pressure Drop | 14.3

## CHW Circuit Setter
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: CHW CIRCUIT SETTERS |  |  |  | Service: CHILLED WATER
Asset | Location | MFG | Model | Size | Design GPM | Delta P | Final GPM | % to Design
FCU-2008D | 10-2008 | VICTAULIC |  |  | 24 |  |  | 0
FCU-2004 | 10-2008 | VICTAULIC |  |  | 4 |  |  | 0
FCU-ST01 | 10-ST-01 | VICTAULIC |  |  | 11 |  |  | 0
FCU-2008E | 10-2008 | VICTAULIC |  |  | 24 |  |  | 0
AHU-8951 | 10-2008 | VICTAULIC |  | 2 | 39 |  |  | 0
AHU-8952 | 10-2008 | VICTAULIC |  | 3 | 440 |  |  | 0
FCU-2008C | 10-2008 | VICTAULIC |  |  | 24 |  |  | 0
AHU-8902 | 10-2008 | VICTAULIC |  | 3 | 193 |  |  | 0
AHU-8903 | 10-2008 | VICTAULIC |  | 3 | 193 |  |  | 0
FCU-2005 | 10-2008 | VICTAULIC |  |  | 6 |  |  | 0
FCU-2000 | 10-2008 | VICTAULIC |  |  | 20 |  |  | 0
FCU-2008B | 10-2008 | VICTAULIC |  |  | 24 |  |  | 0
AHU-8901 | 10-2008 | VICTAULIC |  | 2 | 62 |  |  | 0
FCU-2008A | 10-2008 | VICTAULIC |  |  | 24 |  |  | 0

## HW Circuit Setter
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: HW CIRCUIT SETTERS |  |  |  | Service: HOT WATER
Asset | Location | MFG | Model | Size | Design GPM | Delta P | Final GPM | % to Design
FCU-ST01 | 10-ST-01 | VICTAULIC |  |  | 4 |  |  | 0
RHC-2009 | 10-2003 | VICTAULIC |  |  | 1.93 |  |  | 0
FCU-2008E | 10-2008 | VICTAULIC |  |  | 7 |  |  | 0
RHC-2007 | 10-2008 | VICTAULIC |  |  | 2.7 |  |  | 0
RHC-1017 | 10-2008 | VICTAULIC |  |  | 1.23 |  |  | 0
RHC-1018 | 10-2008 | VICTAULIC |  |  | 1.12 |  |  | 0
RHC-1001 | 10-2008 | VICTAULIC |  |  | 1.93 |  |  | 0
RHC-1003 | 10-2008 | VICTAULIC |  |  | 2.31 |  |  | 0
RHC-1005 | 10-2008 | VICTAULIC |  |  | 5.98 |  |  | 0
AHU-8952 | 10-2008 | VICTAULIC |  | 1.5 | 84 |  |  | 0
AHU-8951 | 10-2008 | VICTAULIC |  | 1.5 | 7 |  |  | 0
RHC-1000B | 10-2008 | VICTAULIC |  |  | 54 |  |  | 0
RHC-1000A | 10-2008 | VICTAULIC |  |  | 54 |  |  | 0
FCU-2008C | 10-2008 | VICTAULIC |  |  | 7 |  |  | 0
AHU-8901 | 10-2008 | VICTAULIC |  | 2 | 18 |  |  | 0
RHC-2015 | 10-2008 | VICTAULIC |  |  | 0.5 |  |  | 0
RHC-1016A | 10-2008 | VICTAULIC |  |  | 30.72 |  |  | 0
RHC-1016B | 10-2008 | VICTAULIC |  |  | 30.72 |  |  | 0
RHC-1021 | 10-2008 | VICTAULIC |  |  | 0.77 |  |  | 0
FCU-2008B | 10-2008 | VICTAULIC |  |  | 7 |  |  | 0
FCU-2008A | 10-2008 | VICTAULIC |  |  | 7 |  |  | 0
RHC-0801F | 10-2008 | VICTAULIC |  |  | 70.76 |  |  | 0
FCU-2008D | 10-2008 | VICTAULIC |  |  | 7 |  |  | 0
RHC-0801E | 10-2008 | VICTAULIC |  |  | 70.76 |  |  | 0
RHC-8951 | 10-2008 | VICTAULIC |  |  | 16.39 |  |  | 0
RHC-0801C | 10-2008 | VICTAULIC |  |  | 26.22 |  |  | 0
RHC-0801D | 10-2008 | VICTAULIC |  |  | 14.65 |  |  | 0
RHC-0801B | 10-2008 | VICTAULIC |  |  | 70.76 |  |  | 0
RHC-0801A | 10-2008 | VICTAULIC |  |  | 70.76 |  |  | 0

## GLYCOL Circuit Setter (1)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: GLYCOL CIRCUIT SETTERS |  |  |  | Service: CHILL ROOM 08-0800
Asset | Location | MFG | Model | Size | Design GPM | Delta P | Final GPM | % to Design
GFCU-8863A | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863B | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863C | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863D | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863E | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863F | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863G | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863H | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863J | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863K | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863L | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863M | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863N | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8863P | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
[5 empty] | 168 |  | 0 | 0
GFCU-8864A | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864B | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864C | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864D | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864E | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864F | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864G | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864H | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864J | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864K | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864L | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864M | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864N | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864P | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8864Q | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
[5 empty] | 180 |  | 0 | 0

## GLYCOL Circuit Setter (2)
National TAB
Project: Eli Lilly Buildings 8 & 10
Address: 1420 Concord Pkwy South, Concord, NC 28027
Asset: GLYCOL CIRCUIT SETTERS |  |  |  | Service: CHILL ROOM 08-0800
Asset | Location | MFG | Model | Size | Design GPM | Delta P | Final GPM | % to Design
GFCU-8861A | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861B | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861C | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861D | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861E | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861F | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861G | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861H | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861J | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861K | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861L | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861M | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861N | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861P | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8861Q | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
[5 empty] | 180 |  | 0 | 0
GFCU-8862A | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862B | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862C | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862D | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862E | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862F | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862G | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862H | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862J | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862K | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862L | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862M | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862N | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862P | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
GFCU-8862Q | 08-0800 | VICTAULIC |  |  | 12 |  |  | 0
[5 empty] | 180 |  | 0 | 0