## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9348 | 8320 | 8608 | 1180 | 740 | 12.42% | 7.916%
AC-2 | SERVING | 5250 | 5065 | 3975 | 4278 | 1275 | 787 | 24.29% | 15.54%
AC-3 | DINING | 6000 | 6063 | 3975 | 5556 | 2025 | 507 | 33.75% | 8.362%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1952
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1401 | 1437
EF-3 | RESTROOM | [12 empty] | 300 | 303
TOTALS |  | 20750 | 20476 | 16270 | 18442 | 4480 | 2034 |  |  | 0 | 0 | 3313 | 3389 | 300 | 303
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4480 | 2034 |  | FRONT |  | -0.009 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3613 | 3692 |  | SIDE |  | -0.0086 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 867 | -1658 |  | REAR |  | -0.0102 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0092667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390