## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2400 | 2992 | 2000 | 2389 | 400 | 603 | 16.67% | 20.15%
RTU-2 | KITCHEN | 3000 | 3018 | 2425 | 2495 | 575 | 523 | 19.17% | 17.33%
KEF-1 | HOOD 2 | [10 empty] | 800 | 852
EF-2 | RESTROOMS | [12 empty] | 150 | 152
EF-3 | TRASH ROOM | [12 empty] | 200 | 212
EF-4 | SEVER ROOM | [12 empty] | 100 | 107
EF-5 | PUMP ROOM | [12 empty] | 150 | 142
TOTALS |  | 5400 | 6010 | 4425 | 4884 | 975 | 1126 |  |  | 0 | 0 | 800 | 852 | 600 | 613
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 975 | 1126 |  | FRONT |  | -0.0038 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1400 | 1465 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -425 | -339 |  | REAR |  | -0.0052 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0045 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0