## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN |  | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9115 | 8250 | 7803 | 1250 | 1312 | 13.16% | #REF!
AC-2 | SERVING, DRIVE THRU | 5600 | 5756 | 4025 | 4223 | 1575 | 1533 | 28.12% | 26.63%
AC-3 | DINING | 6400 | 5917 | 4575 | 4008 | 1825 | 1909 | 28.52% | 32.26%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1904
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1452
EF-3 | RESTROOM | [12 empty] | 300 | 313
TOTALS |  | 21500 | 20788 | 16850 | 16034 | 4650 | 4754 |  |  | 0 | 0 | 3314 | 3356 | 300 | 313
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4754 |  | FRONT |  | 0.0034 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3669 |  | SIDE |  | 0.0024 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1036 | 1085 |  | REAR |  | 0.0034 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0030667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390