## Report Sheet
STORE #: | 3444 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | GREEN TOWNSHIP, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-03-24 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ078N12B2B5HAA2A2 | N1F9014084 | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1748 | 1744 | 845 | 820 | 1.5 | 204.6 | 204.6 | 3 | 5 | 5.73 | 3.76 | 1.9598 | 1.286 | -34.38%
YORK | ZJ090N18D2B5HAA2A2 | N1H9179872 | RTU-2 | DINING | 1000 | 215 | 1000 | 1004 |  | 1754 | 1754 | 974 | 974 | 3 | 204.8 | 204.8 | 3 | 9.4 | 8.41 | 8.41 | 2.8792 | 2.8792 | 0%
CAPTIVE AIRE | A1-D.25-G10 | 3836625 | MUA-1 | HOOD 1 | 1950 | 1289 | 1700 | 1662 | No | 1786 | 1754 | 880 | 1135 | 2 | 205.3 | 203.3 | 3 | 5.38 | 2.49 | 3.15 | 0.85453 | 1.0705 | 25.27%
CAPTIVE AIRE | NCA24HPFA | 3836625 | EF-1 | HOOD 1 | 3200 | 2169 | 2450 | 2272 | No | 1763 | 1754 | 883 | 925 | 2 | 204.9 | 201.5 | 3 | 5.38 | 3.86 | 3.98 | 1.3221 | 1.3406 | 1.398%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 1504 | 2700 | 2666 |  | FRONT DOOR |  | -0.001 |  |  | INITIAL | 7.0156 | 1504
|  |  | TOTAL EXHAUST |  | 3350 | 2319 | 2600 | 2422 |  | BACK DOOR |  | 0.014 |  |  | FINAL | 6.5763 | 2666
|  |  | NET AIRFLOW |  | 100 | -815 | 100 | 244 |  | AVERAGE |  | 0.0065 |  |  | ∆ | -0.43932 | 1162
Issue List
Unit # | Description
Select from drop down list
MUA | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
Z
Additional Notes: | [20 empty] | 3

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.