## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3500 | 2922 | 3000 | 2386 | 500 | 536 | 14.29% | 18.34%
RTU-2 | DINING | 4000 | 3929 | 3000 | 2898 | 1000 | 1031 | 25% | 26.24%
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1303
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2507
EF-2 | RESTROOM | [12 empty] | 150 | 140
TOTALS |  | 7500 | 6851 | 6000 | 5284 | 1500 | 1567 |  |  | 1300 | 1303 | 2550 | 2507 | 150 | 140
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2870 |  | FRONT |  | 0.001 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2700 | 2647 |  | SIDE |  | 0.001 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 223 |  | REAR |  | 0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.001 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165x19 |  | 1300 |  | 2550 |  | -1250