## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | COOKLINE | 2400 | 2403 | 2100 | 2091 | 300 | 312 | 12.5% | 12.98%
RTU-2 | DINING/RR | 3000 | 2996 | 2485 | 2996 | 515 |  | 17.17% | 0%
RTU-3 | DINING AREA | 1200 | 1265 | 1030 | 1120 | 170 | 145 | 14.17% | 11.46%
FCU-1 | KITCHEN | 3000 | 2961 | 3000 | 2961 | 0 | 0 | 0% | 0%
ACU-1 | OFFICE |  |  |  |  | 15 | 15 | #DIV/0! | #DIV/0!
MUA-1 | KITCHEN | [8 empty] | 1980 | 1345
EF-1 | HOOD1 | [10 empty] | 767 | 779
EF-2 | HOO2 | [10 empty] | 1708 | 886
EF-3 | RESTROOM | [12 empty] | 300 | 297
TOTALS |  | 9600 | 9625 | 8615 | 9168 | 1000 | 472 |  |  | 1980 | 1345 | 2475 | 1665 | 300 | 297
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2980 | 1817 |  | FRONT |  | 0.018 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 2775 | 1962 |  | SIDE |  | 0.022 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 205 | -145 |  | REAR |  | 0.035 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.025 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2280
TOTAL KITCHEN EXHAUST |  | 2475
NET AIRFLOW |  | -195 | 0
Return trip required to check hoods, and balance out Captive Aire Unit. Balance of Captive Air Unit was unable to be done due to Issues with Hood fans and MAU VFD.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0