## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN/ BOH | 8750 | 8944 | 7000 | 7235 | 1750 | 1709 | 20% | 19.11%
AC-2 | DRIVE THRU | 5250 | 5124 | 4000 | 3903 | 1250 | 1221 | 23.81% | 23.83%
AC-3 | DINNING/ RR | 5250 | 5286 | 3979 | 4037 | 1271 | 1249 | 24.21% | 23.63%
AC-4 | BOH | 1875 | 1901 | 1375 | 1407 | 500 | 494 | 26.67% | 25.99%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD 1 | [10 empty] | 1913 | 1908
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1496
EF-3 | RESTROOMS | [12 empty] | 375 | 387
EF4 | HD 2
EF 5 | HD L1
TOTALS |  | 21125 | 21255 | 16354 | 16582 | 4771 | 4673 |  |  | 0 | 0 | 3315 | 3404 | 375 | 387
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4771 | 4673 |  | FRONT |  | 0.02 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3791 |  | SIDE |  | 0.017 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1081 | 882 |  | REAR |  | 0.023 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.02 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390