## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FRONT SALES/ENTRY | 3150 |  | 2678 | -472 | 472 | 472 | 14.98% | #DIV/0!
RTU-2 | FRONT SALES/OFFICE/PHOTO | 3125 |  | 2656 | -469 | 469 | 469 | 15.01% | #DIV/0!
RTU-3 | REAR SALES | 3150 |  | 2678 | -472 | 472 | 472 | 14.98% | #DIV/0!
RTU-4 | REAR SALES/BREAKROOM | 2730 |  | 2321 | -409 | 409 | 409 | 14.98% | #DIV/0!
RTU-5 | STOCK ROOM | 1600 |  | 1360 | -240 | 240 | 240 | 15% | #DIV/0!
RTU-6 | PHARMACY | 2100 |  | 2096 | 0 | 4 |  | 0.1905% | #DIV/0!
EF-1 | 1-HOUR PHOTO
EF-2 | EMPLOYEE RESTROOM | [12 empty] | 300 | 314
EF-3 | MENS + WOMENS RESTROOM | [12 empty] | 500 | 508
TOTALS |  | 15855 | 0 | 13789 | -2062 | 2066 | 2062 |  |  | 0 | 0 | 0 | 0 | 800 | 822
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2066 | 2062 |  | FRONT | [10 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 800 | 822 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1266 | 1240 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE | [5 empty] | DESIGN PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 1
TRUE
[11 empty] | ACTUAL PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 1
NOTES:
DESIGN NET PRESSURIZATION CALCULATION
158.2%