## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FRONT SALES/ENTRY | 3150 | 3060 | 2678 | 2576 | 472 | 484 | 14.98% | 15.82%
RTU-2 | FRONT SALES/OFFICE/PHOTO | 3125 | 3026 | 2656 | 2545 | 469 | 481 | 15.01% | 15.9%
RTU-3 | REAR SALES | 3150 | 3390 | 2800 | 3018 | 350 | 372 | 11.11% | 10.97%
RTU-4 | REAR SALES/BREAKROOM | 2730 | 0 | 2430 | 0 | 300 | 0 | 10.99% | #DIV/0!
RTU-5 | STOCK ROOM | 1600 | 1633 | 1425 | 1446 | 175 | 187 | 10.94% | 11.45%
RTU-6 | PHARMACY | 2100 | 1979 | 2100 | 1979 | 0 | 0 | 0% | 0%
EH-1 | ENTRANCE DOORS | 2000 | 2093
EF-2 | EMPLOYEE RESTROOM | [12 empty] | 300 | 314
EF-3 | MENS + WOMENS RESTROOM | [12 empty] | 500 | 508
TOTALS |  | 17855 | 15181 | 14089 | 11564 | 1766 | 1524 |  |  | 0 | 0 | 0 | 0 | 800 | 822
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1766 | 1524 |  | FRONT |  | 0.0104 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 800 | 822 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 966 | 702 |  | REAR |  | 0.0121 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01125 |  |  |  | DESIGN PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 1
TRUE
[11 empty] | ACTUAL PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 1
NOTES:
DESIGN NET PRESSURIZATION CALCULATION
120.8%