## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING 1 | 2350 | 2311 | 2035 | 2005 | 315 | 306 | 13.4% | 13.24%
RTU-2 | DINING2 | 2350 | 2344 | 2035 | 2010 | 315 | 334 | 13.4% | 14.25%
RTU-3 | KITCHEN | 2230 | 2234 | 0 | 0 | 2230 | 2234 | 100%
RTU-4 | KITCHEN | 1800 | 1819 | 1350 | 1698 | 450 | 121 | 25%
KEF-1 | HOOD 1 | [10 empty] | 2348 | 2416
EF-1 | RESTROOMS | [12 empty] | 500 | 367
TOTALS |  | 8730 | 8708 | 5420 | 5713 | 3310 | 2995 |  |  | 0 | 0 | 2348 | 2416 | 500 | 367
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3310 | 2995 |  | FRONT |  | 0.0056 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2848 | 2783 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 462 | 212 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0056 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 0 | 2355
TOTAL KITCHEN EXHAUST |  | 0 | 2416
NET AIRFLOW |  | 0 | -61
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0