## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6537 | 4275 | 4648 | 1875 | 1889 | 30.49% | 28.9%
RTU-2 | KITCHEN | 6150 | 6010 | 4300 | 4137 | 1850 | 1873 | 30.08% | 31.16%
EF-1A | MOP ROOM | [12 empty] | 75 | 73
PRV-1 | RESTROOM | [12 empty] | 300 | 318
PRV-2 | HOOD 1 | [10 empty] | 1500 | 1734
PRV-3 | HOOD 2 | [10 empty] | 1500 | 1629
TOTALS |  | 12300 | 12547 | 8575 | 8785 | 3725 | 3762 |  |  | 0 | 0 | 3000 | 3363 | 375 | 391
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3725 | 3762 |  | FRONT |  | 0.0027 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3375 | 3754 |  | SIDE |  | 0.0003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 350 | 8 |  | REAR |  | 0.0018 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0016 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0