## Report Sheet
STORE #: | #3754 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | Groveport, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-16 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | Tyler Youells, Dylan Chrisman | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ090N12R2B5EAA2A2 | N2F0896290 | RTU-1 | KITCHEN | 500 | 0 | 260 |  |  | 1744 |  | 1050 |  | 3 | 210.2 |  | 3 | 8.3 | 11.5 |  | 4.0408 | 0 | -100%
YORK | ZJ120N24R2B5EAA2A2 | N2G0996469 | RTU-2 | DINING | 1000 | 1120 | 750 |  |  | 726 |  | 1034 |  | 3 | 210.3 |  | 3 | 8.3 | 8.73 |  | 3.069 | 0 | -100%
CAPTIVE AIRE | A1-D.250-G10 | 4358245 | MUA-1 | HOOD 1 | 1950 | 1552 | 1700 |  | Choose Yes or No: | 1779 |  | 1138 |  | 2 | 209.3 |  | 3 | 5.9 | 2.93 |  | 1.0251 | 0 | -100%
CAPTIVE AIRE | NCA24HPFA | 4358245 | EF-1 | HOOD 1 | 3200 | 2916 | 2450 |  | Choose Yes or No: | 1768 |  | 856 |  | 2 | 208.8 |  | 3 | 5.9 | 3.58 |  | 1.2496 | 0 | -100%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150 | [5 empty] | 2
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 2672 | 2710 | 0 |  | FRONT DOOR |  |  |  |  | INITIAL | 9.3845 | 2672
|  |  | TOTAL EXHAUST |  | 3350 | 3066 | 2600 | 150 |  | BACK DOOR |  |  |  |  | FINAL | 0 | 0
|  |  | NET AIRFLOW |  | 100 | -394 | 110 | -150 |  | AVERAGE |  | 0 |  |  | ∆ | 9.3845 | 2672
Issue List
Unit # | Description
Select from drop down list

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.