## 2EP-2925
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
CARRIER | 48HCFD11A2M5A6F4J0 | 1122P98761 | RTU-1 | KITCHEN | 500 | 395 | 0 | 0 | 1741/1742 | 894/895 | 3.7 | 212.3 | 3 | 9.2 | 4.87 | 4.83 | 1.9586 | 1.9425 | -0.8214%
CARRIER | 48HCFD11A2M5A6F4J0 | 1122P98760 | RTU-2 | DINING | 1000 | 809 | 1000 | 1002 | 1729/1725 | 863/865 | 3.7 | 212.7 | 3 | 9.2 | 7.33 | 7.44 | 2.9479 | 2.9922 | 1.501%
CAPTIVE-AIRE | A1-D.250-15D | 5166348 | MUA-1 | HOOD 1 | 1775 | 1910 | 1500 | 1539 | 1942/1591 | 1942/1591 | 2 | 98V | 3 | 5.48 | 5 | 4 | 1.8248 | 1.4599 | -20%
CAPTIVE-AIRE | DU240HFA | 5166348 | EF-1 | HOOD 1 | 2925 | 2997 | 2200 | 2170 | 707/550 | 707/550 | 3 | 55V | 3 | 9.2 | 5.6 | 4.3 | 1.8261 | 1.4022 | -23.21%
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150 | [10 empty] | #DIV/0!
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3275 | 3114 | 2500 | 2541 | 0.011 | FRONT DOOR | 7.5574 | 3114 | INITIAL
|  |  | TOTAL EXHAUST |  | 3075 | 3147 | 2350 | 2320 | 0.015 | BACK DOOR | 6.7967 | 2541 | FINAL
|  |  | NET AIRFLOW |  | 200 | -33 | 150 | 221 | 0.013 | AVERAGE | -10.07% | 573 | NET CHANGE

## 2EP-3200
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE |  |  | RTU-1 | KITCHEN | 500 |  | 0 |  |  | 890 / 790 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
TRANE |  |  | RTU-2 | DINING | 1000 |  | 1000 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | MUA-1 | HOOD 1 | 1950 |  | 1875 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | EF-1 | HOOD 1 | 3200 | 0 | 2650 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3450 | 0 | 2875 | 0 |  | FRONT DOOR | #DIV/0! | 0 | INITIAL
|  |  | TOTAL EXHAUST |  | 3350 | 150 | 2800 | 150 |  | BACK DOOR | #DIV/0! | 0 | FINAL
|  |  | NET AIRFLOW |  | 100 | -150 | 75 | -150 |  | AVERAGE | #DIV/0! | 0 | NET CHANGE