## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | ENTRY | 1600 | 1583 | 1400 | 1365 | 200 | 218 | 12.5% | 13.77%
RTU-2 | BAR DINING | 4000 | 3944 | 3240 | 3176 | 760 | 768 | 19% | 19.47%
RTU-3 | BAR DINING | 1280 | 1314 | 1080 | 1105 | 200 | 209 | 15.62% | 15.91%
RTU-4 | RR | 600 | 940 | 450 | 786 | 150 | 154 | 25% | 16.38%
RTU-5 | PRIVATE I | 960 | 988 | 760 | 805 | 200 | 183 | 20.83% | 18.52%
RTU-6 | PRIVATE II | 2400 | 2325 | 1990 | 1937 | 410 | 388 | 17.08% | 16.69%
RTU-7 | PRIVATE III | 2400 | 2504 | 1880 | 1942 | 520 | 562 | 21.67% | 22.44%
RTU-8 | MAIN D II | 3200 | 3126 | 2160 | 2101 | 1040 | 1025 | 32.5% | 32.79%
RTU-9 | MAIN D I | 4000 | 3962 | 3160 | 3144 | 840 | 818 | 21% | 20.65%
RTU-10 | ROOM 79 | 2400 | 2505 | 2185 | 2299 | 215 | 206 | 8.958% | 8.224%
RTU-11 | OFFICES | 4800 | 4919 | 3925 | 4083 | 875 | 836 | 18.23% | 17%
RTU-12 | SERVICE | 4800 | 4651 | 3925 | 3751 | 875 | 900 | 18.23% | 19.35%
RTU-13 | BAR | 2720 | 2766 | 2240 | 2323 | 480 | 443 | 17.65% | 16.02%
MUA-1 | DIFFUSER | [8 empty] | 300 | 290
EF-1 | EXH-L | [8 empty] | 564 | 532 | 1311 | 1315
EF-2 | EXH-M | [8 empty] | 990 | 1043 | 2250 | 2271
EF-3 | EXH-R | [8 empty] | 1139 | 1094 | 1808 | 1835
EF-4 | PREP | [10 empty] | 1800 | 1864
EF-1 | RR | [12 empty] | 600 | 551
EF-2 | DISHES | [12 empty] | 600 | 608
EF-3 | MOP | [12 empty] | 100 | 107
EF-4 | TOILET | [12 empty] | 75 | 78
EF-5 | SMOKER | [12 empty] | 1000 | 1343
TOTALS |  | 35160 | 35527 | 28395 | 28817 | 6765 | 6710 |  |  | 2993 | 2959 | 7169 | 7285 | 2375 | 2687
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 9758 | 9669 |  | FRONT |  | [1] | [8 empty] | #DIV/0! | #DIV/0! | TRUE
TOTAL EXHAUST |  | 9544 | 9972 |  | SIDE |  | [1] |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 214 | -303 |  | REAR |  | [1] | [8 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
[1] Unable to measure Building Pressure as building is not completely sealed. [2] EF-2 (Dishwasher) and EF-5 (Smoker) run Intermittently
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0