## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3451 | 2575 | 2613 | 825 | 838 | 24.26% | 24.28%
RTU-2 | DINING | 3400 | 3456 | 2650 | 2695 | 750 | 761 | 22.06% | 22.02%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1879
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3175
EF-2 | RESTROOM | [12 empty] | 150 | 153
TOTALS |  | 6800 | 6907 | 5225 | 5308 | 1575 | 1599 |  |  | 1950 | 1879 | 3200 | 3175 | 150 | 153
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3525 | 3478 |  | FRONT |  | -0.031 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 3350 | 3328 |  | SIDE |  | 0.002 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 175 | 150 |  | REAR |  | 0.0013 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0092333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] STRONG WINDS GUSTING ONTO FRONT DO0R CAUSING NEGATIVE PRESSURE READING.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250