## Report Sheet
STORE #: | 2348 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | CUYAHOGA FALLS,OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-31 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | MOHAMMED OUARD | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
TRANE | YHC060F3RMA07H2C1A2A | 143212269L | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1776 | 1776 | 820 | 820 | 1 | 208 | 208 | 3 | 4 | 2.3 | 2.3 | 0.79971 | 0.79971 | 0%
TRANE | YHC092F3RHA0BH0C1A2A | 143212459L | RTU-2 | DINING | 1000 | 0 | 1000 | 1035 |  | 1070 | 1070 | 1070 | 1070 | 3.8 | 207 | 207 | 3 | 8.5 | 2.4 | 2.1 | 0.83047 | 0.72666 | -12.5%
CAPTIVE AIRE | A1-D.250-G10 | 2074552 | MUA-1 | HOOD 1 | 1775 | 1461 | 1500 | 1461 | No | 1768 | 1768 | 1205 | 1205 | 2 | 207 | 207 | 3 | 6.88 | 4.2 | 4.2 | 1.4533 | 1.4533 | 0%
CAPTIVE AIRE | NCA24HPFA | 2074552 | EF-1 | HOOD 1 | 2925 | 2595 | 2200 | 2308 | No | 1774 | 1776 | 788 | 698 | 2 | 207 | 207 | 3 | 5.95 | 3.8 | 3.25 | 1.3149 | 1.1246 | -14.47%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | [7 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3275 | 1461 | 2500 | 2496 |  | FRONT DOOR |  | 0.0005 |  |  | INITIAL | 4.3984 | 1461
|  |  | TOTAL EXHAUST |  | 3075 | 2745 | 2350 | 2458 |  | BACK DOOR |  | 0.0015 |  |  | FINAL | 4.1043 | 4804
|  |  | NET AIRFLOW |  | 200 | -1284 | 150 | 38 |  | AVERAGE |  | 0.001 |  |  | ∆ | 0.29412 | -3343
Issue List
Unit # | Description
Select from drop down list
RTU1 AND RTU 2 MISSING OA FILTERS .

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.