## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-A1 | KITCHEN | 3570 | 3606 | 1070 | 1185 | 2500 | 2421 | 70.03% | 67.14%
RTU-B1 | DINING | 3410 | 3800 | 1110 | 1437 | 2300 | 2363 | 67.45% | 62.18%
EF-A1 | GRILL HOOD | [10 empty] | 2550 | 2419
EF-B1 | FRYER HOOD | [10 empty] | 1216 | 1336
EF-C1 | RESTROOMS | [12 empty] | 200 | 211
TOTALS |  | 6980 | 7406 | 2180 | 2622 | 4800 | 4784 |  |  | 0 | 0 | 3766 | 3755 | 200 | 211
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4800 | 4784 |  | FRONT |  | 0.022 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3966 | 3966 |  | SIDE |  | 0.022 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 834 | 818 |  | REAR |  | 0.022 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.022
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0