## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Kitchen | 2000 | 2012 | 1600 | 1612 | 400 | 400 | 20% | 19.88%
RTU-2 | Dining | 4000 | 3765 | 3200 | 2893 | 800 | 872 | 20% | 23.16%
MUA-1 | Kitchen | [8 empty] | 2750 | 0
KEF-1 | Hood1 | [10 empty] | 1800 | 1698
KEF-2 | Hood2 | [10 empty] | 1800 | 1965
EF-3 | RR | [12 empty] | 330 | 330
TOTALS |  | 6000 | 5777 | 4800 | 4505 | 1200 | 1272 |  |  | 2750 | 0 | 3600 | 3663 | 330 | 330
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3950 | 1272 |  | FRONT |  | -0.0678 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3930 | 3993 |  | SIDE |  | N/A |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 20 | -2721 |  | REAR |  | -0.0693 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.06855 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0