## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3850 | 3946 | 1390 | 1593 | 2460 | 2353 | 63.9% | 59.63%
RTU-2 | DINING | 2050 | 2038 | 500 | 556 | 1550 | 1482 | 75.61% | 72.72%
KEF-1 | KITCHE HD | [10 empty] | 2110 | 2134
KEF-2 | KITCHEN HD | [10 empty] | 1215 | 1250
EF-1 | RESTROOMS | [12 empty] | 300 | 436
TOTALS |  | 5900 | 5984 | 1890 | 2149 | 4010 | 3835 |  |  | 0 | 0 | 3325 | 3384 | 300 | 436
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4010 | 3835 |  | FRONT |  | 0.019 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3625 | 3820 |  | SIDE |  | 0.017 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 385 | 15 |  | REAR |  | 0.021 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.019
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0