## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | dining | 2000 | 956 | 1250 | 582 | 750 | 374 | 37.5% | 39.12%
RTU-2 | kitchen | 3000 | 1525 | 2500 | 1132 | 500 | 393 | 16.67% | 25.77%
RTU-3 | restrooms/BOH | 1400 | 937 | 900 | 544 | 500 | 393 | 35.71% | 41.94%
MUA | [9 empty] | 1400 | 1130
KEF-1 | fryer | [10 empty] | 894 | 894
KEF-2 | griddle | [10 empty] | 798 | 798
KEF-3 | toaster | [10 empty] | 1119 | 1119
EF-4 | mens rr | [12 empty] | 77 | 77
EF-5 | womens rr | [12 empty] | 79 | 79
TOTALS |  | 6400 | 3418 | 4650 | 2258 | 1750 | 1160 |  |  | 1400 | 1130 | 2811 | 2811 | 156 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3150 | 2290 |  | FRONT |  | 0.0031 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2967 | 2967 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 183 | -677 |  | REAR |  | -0.0126 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.00475 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0